## DASHBOARD
SPDC |  |  | DAILY PROGRESS REPORT | [10 empty] | Report Date |  |  | 2026-07-31
[14 empty] | Data Date |  |  | 2026-07-31
|  |  | ELECTRICAL WORKS PACKAGE — HT / LT, CABLING, LIGHTING & EARTHING | [10 empty] | Report No. / Day |  |  | DPR/ELE-027 ¦ Friday | [5 empty] | S-CURVE DATA (not printed)
Project Name |  | <Client / Project Name> | [5 empty] | Contract / PO Ref. |  | <Work Order No. & Date> |  |  |  | PROJECT HEALTH | [8 empty] | DATE | PLANNED CUM % | ACTUAL CUM % | NOTE
Project Manager |  | <PMC Project Manager> | [5 empty] | Contract Completion |  | 2026-09-30 |  |  |  | Overall Status |  |  |  | BEHIND PROGRAMME |  |  |  |  | 2026-07-01 | 0% | 0% | from INPUT sheet section 14
Contractor / Vendor |  | <Executing Agency / PEB Vendor> | [5 empty] | Calendar / Weather |  | 6 Days / Week – 8 hrs ¦ Partly Cloudy, 32 °C |  |  |  | Critical / High issues open |  |  |  | 3 |  |  |  |  | 2026-07-06 | 0% | 0.4005% | from INPUT sheet section 14
Location |  | <Plot / GIDC / District> | [5 empty] | Contract Value (₹ Lakh) |  | 154.748 |  |  |  | Approvals pending > 7 days |  |  |  | 3 |  |  |  |  | 2026-07-11 | 0% | 0.8368% | from INPUT sheet section 14
1. KEY PERFORMANCE INDICATORS (all calculated — nothing is typed on this sheet) | [22 empty] | 2026-07-16 | 0.1154% | 0.8368% | from INPUT sheet section 14
PLANNED % |  |  | ACTUAL % |  |  | VARIANCE |  |  | SPI |  |  | EARNED VALUE ₹ L |  |  | VALUE DONE TODAY ₹ |  |  | ITEMS DELAYED |  | HRS LOST TODAY |  |  | 2026-07-21 | 0.404% | 0.8368% | from INPUT sheet section 14
0.9811% |  |  | 0.8368% |  |  | -0.1443% |  |  | 0.85294 |  |  | 1.295 |  |  | 18500 |  |  | 0 |  | 6 |  |  | 2026-07-26 | 0.6926% | 0.8368% | from INPUT sheet section 14
2. QUANTITY / PHYSICAL PROGRESS — ITEM-WISE (basis of the % complete above) | [22 empty] | 2026-07-31 | 0.9811% | 0.8368% | ◄ today – from the quantity table
SL | DESCRIPTION OF ITEM |  |  |  | UNIT | SCOPE QTY | RATE ₹ | WEIGHT-AGE % | START | FINISH | DAYS +/− | PLANNED % | CUM QTY PREV. | QTY TODAY | CUM QTY TO DATE | BALANCE QTY | % COMPL. | EARNED ₹ TODAY | WTD. PLANNED % | WTD. ACTUAL % | STATUS |  | 2026-08-05 | 1.27% |  | from INPUT sheet section 14
1 | HT panel / VCB 11 kV with accessories |  |  |  | NOS | 2 | 685000 | 8.853% | 2026-09-01 | 2026-10-10 | 71 | 0% | 0 | 0 | 0 | 2 | 0% | 0 | 0% | 0% | Not Started | ELE-10 | 2026-08-10 | 1.558% |  | from INPUT sheet section 14
2 | Transformer 1250 kVA – erection & oil filling |  |  |  | NOS | 2 | 1450000 | 18.74% | 2026-09-15 | 2026-10-25 | 86 | 0% | 0 | 0 | 0 | 2 | 0% | 0 | 0% | 0% | Not Started | ELE-10 | 2026-08-15 | 1.941% |  | from INPUT sheet section 14
3 | HT cable 11 kV 3C x 240 sqmm laying |  |  |  | RM | 320 | 2850 | 5.893% | 2026-09-20 | 2026-10-30 | 91 | 0% | 0 | 0 | 0 | 320 | 0% | 0 | 0% | 0% | Not Started | ELE-10 | 2026-08-20 | 2.735% |  | from INPUT sheet section 14
4 | LT main panel (PCC) erection |  |  |  | NOS | 1 | 1850000 | 11.95% | 2026-09-25 | 2026-11-05 | 97 | 0% | 0 | 0 | 0 | 1 | 0% | 0 | 0% | 0% | Not Started | ELE-20 | 2026-08-25 | 3.672% |  | from INPUT sheet section 14
5 | MCC & distribution boards |  |  |  | NOS | 14 | 145000 | 13.12% | 2026-10-01 | 2026-11-15 | 107 | 0% | 0 | 0 | 0 | 14 | 0% | 0 | 0% | 0% | Not Started | ELE-20 | 2026-08-30 | 4.608% |  | from INPUT sheet section 14
6 | LT power cable 3.5C x 300 sqmm laying |  |  |  | RM | 860 | 1650 | 9.17% | 2026-10-05 | 2026-11-20 | 112 | 0% | 0 | 0 | 0 | 860 | 0% | 0 | 0% | 0% | Not Started | ELE-20
7 | Cable tray, ladder & support system |  |  |  | RM | 1250 | 780 | 6.301% | 2026-08-15 | 2026-10-20 | 81 | 0% | 0 | 0 | 0 | 1250 | 0% | 0 | 0% | 0% | Not Started | ELE-20
8 | Internal wiring points – light & power |  |  |  | NOS | 640 | 1250 | 5.17% | 2026-09-10 | 2026-11-10 | 102 | 0% | 0 | 0 | 0 | 640 | 0% | 0 | 0% | 0% | Not Started | ELE-30
9 | LED high bay, street & flame proof fittings |  |  |  | NOS | 186 | 4800 | 5.769% | 2026-10-10 | 2026-11-25 | 117 | 0% | 0 | 0 | 0 | 186 | 0% | 0 | 0% | 0% | Not Started | ELE-30
10 | Conduits, raceways & accessories |  |  |  | RM | 2400 | 165 | 2.559% | 2026-08-20 | 2026-10-30 | 91 | 0% | 0 | 0 | 0 | 2400 | 0% | 0 | 0% | 0% | Not Started | ELE-30
11 | Earthing pits with GI / copper strip |  |  |  | NOS | 28 | 18500 | 3.347% | 2026-07-15 | 2026-09-10 | 41 | 29.31% | 6 | 1 | 7 | 21 | 25% | 18500 | 0.9811% | 0.8368% | In Progress | ELE-40
12 | Lightning protection with air terminals |  |  |  | LS | 1 | 385000 | 2.488% | 2026-09-05 | 2026-10-15 | 76 | 0% | 0 | 0 | 0 | 1 | 0% | 0 | 0% | 0% | Not Started | ELE-40
13 | Cable termination, glanding & megger test |  |  |  | NOS | 320 | 850 | 1.758% | 2026-10-20 | 2026-12-05 | 127 | 0% | 0 | 0 | 0 | 320 | 0% | 0 | 0% | 0% | Not Started | ELE-50
14 | Panel testing, relay setting & charging |  |  |  | LS | 1 | 480000 | 3.102% | 2026-11-15 | 2026-12-15 | 137 | 0% | 0 | 0 | 0 | 1 | 0% | 0 | 0% | 0% | Not Started | ELE-50
15 | CEIG statutory inspection & approval |  |  |  | LS | 1 | 275000 | 1.777% | 2026-12-01 | 2026-12-20 | 142 | 0% | 0 | 0 | 0 | 1 | 0% | 0 | 0% | 0% | Not Started | ELE-50
TOTAL / OVERALL PACKAGE PROGRESS |  |  |  |  | ₹ 154.7 Lakh |  |  | 100% | PROGRAMME |  |  | 0.9811% |  |  |  |  | 0.8368% | 18500 | 0.9811% | 0.8368% | BEHIND
3. PROGRESS SUMMARY BY GROUP (value weighted) | [9 empty] | 4. PROGRESS S-CURVE (PLANNED vs ACTUAL)
GROUP |  | DESCRIPTION |  |  | WEIGHTAGE |  | PLANNED % | ACTUAL % | SPI
ELE-10 |  | HT, Transformer & Substation |  |  | 33.49% |  | 0% | 0%
ELE-20 |  | LT Panels, Cabling & Trays |  |  | 40.54% |  | 0% | 0%
ELE-30 |  | Internal Wiring, Lighting & Conduits |  |  | 13.5% |  | 0% | 0%
ELE-40 |  | Earthing & Lightning Protection |  |  | 5.835% |  | 16.81% | 14.34% | 0.85294
ELE-50 |  | Testing, Commissioning & Statutory Approval |  |  | 6.637% |  | 0% | 0%
TOTAL |  |  |  |  | 100% |  | 0.9811% | 0.8368% | 0.85294
5. EARNED VALUE / COMMERCIAL SNAPSHOT (₹ in Lakh)
BAC – Contract value of package | [6 empty] | 154.748
PV – Planned Value (BAC × Planned %) | [6 empty] | 1.5183
EV – Earned Value (BAC × Actual %) | [6 empty] | 1.295
AC – Certified / paid to date | [6 empty] | 1.4
SV – Schedule Variance (EV − PV) | [6 empty] | -0.22328
CV – Cost Variance (EV − AC) | [6 empty] | -0.105
CPI ¦ EAC (BAC ÷ CPI) | [6 empty] | 0.93 ¦ ₹ 167.3 L
6. MANPOWER DEPLOYED TODAY | [6 empty] | 7. EQUIPMENT UTILIZATION TODAY | [6 empty] | 8. KEY MATERIAL AT SITE
TRADE / CATEGORY |  |  | PLAN | ACTUAL | MAN-DAYS |  | EQUIPMENT |  |  | QTY | WORKED HRS | IDLE HRS | UTIL. % | MATERIAL |  |  | UNIT | OPENING | RECD. | CONSUMED | BALANCE
Electrician |  |  | 10 | 8 | 8.5 |  | Hydra 8 T |  |  | 1 | 4 | 4 | 50% | Cable tray & ladder – perforated |  |  | RM | 420 | 120 | 0 | 540
Cable Jointer |  |  | 4 | 2 | 2.125 |  | Cable Drum Stand & Rollers |  |  | 2 | 6 | 10 | 37.5% | Conduits, bends & accessories |  |  | RM | 680 | 200 | 0 | 880
Fitter – tray & support |  |  | 6 | 5 | 5.3125 |  | Megger / Insulation Tester |  |  | 2 | 3 | 13 | 18.75% | Earthing strip & GI pipe electrodes |  |  | KGS | 480 | 0 | 68 | 412
Helper |  |  | 12 | 9 | 9.5625 |  | Crimping & Hydraulic Tools |  |  | 4 | 18 | 14 | 56.25% | LT / HT cable (on drums) |  |  | RM | 0 | 0 | 0 | 0
Testing Technician |  |  | 2 | 1 | 1 |  | Drilling & Chasing Machines |  |  | 6 | 30 | 18 | 62.5% | Light fittings – LED high bay |  |  | NOS | 0 | 0 | 0 | 0
Supervisor & PMC Staff |  |  | 4 | 4 | 4.5 |  | DG Set & Welding Machine |  |  | 2 | 11 | 5 | 68.75% | Lugs, glands & consumables |  |  | NOS | 640 | 100 | 46 | 694
TOTAL WORKERS / MAN-DAYS |  |  | 38 | 29 | 31 |  | TOTAL / AVERAGE |  |  | 17 | 72 | 64 | 52.94% | Balance = Opening + Received − Consumed · carry Balance forward as tomorrow's Opening on the INPUT sheet
9. QUALITY CONTROL & TESTS TODAY | [6 empty] | 10. HSE / SAFETY STATISTICS | [6 empty] | 11. DELAY / IDLE TIME LOG TODAY
Earth pit resistance readings |  |  |  |  | 5 pits, all < 2 ohm |  | Safe man-hours – today / cumulative |  |  |  |  | 250 / 4,320 |  | CAUSE (CATEGORY) |  |  |  | FROM | TO | HRS LOST | EOT
Insulation (megger) test records |  |  |  |  | Not yet due |  | Days without LTI |  |  |  |  | 122 |  | Shutdown not granted for HT termination (Client / Vendor) |  |  |  | 10:00 | 13:00 | 3 | Yes
Cable schedule vs. drawing verification |  |  |  |  | Under review |  | Electrical work permits issued |  |  |  |  | 3 |  | Rain – outdoor earthing work stopped (Weather) |  |  |  | 15:00 | 16:30 | 1.5 | Review
Panel FAT report received |  |  |  |  | 1 of 3 panels |  | LOTO applied on live circuits |  |  |  |  | Yes – 2 points |  | Cable jointer gang short by 2 nos. (Contractor) |  |  |  | 8:00 | 9:30 | 1.5 | No
Earthing strip welding & painting check |  |  |  |  | 6 joints cleared |  | Work at height permits issued |  |  |  |  | 2 | [5 empty] | 0:00 | 0:00 |  | 0
NCRs open / closed today |  |  |  |  | 0 / 1 |  | Safety observations raised / closed |  |  |  |  | 3 / 3 |  | TOTAL HOURS LOST TODAY | [5 empty] | 6 | 1 EOT
12. DRAWINGS / RFI / MATERIAL APPROVALS PENDING | [10 empty] | 13. ISSUES & RISKS (open items)
REF. NO. |  | DESCRIPTION | [5 empty] | RAISED ON | AGEING | PENDING WITH | ISSUE / RISK DESCRIPTION | [6 empty] | SEVERITY |  | OWNER
RFI-093 |  | Single line diagram rev-3 – approval | [5 empty] | 2026-07-20 | 11 | Consultant | ⚠ Transformer delivery lead time 14 weeks – order not yet released | [6 empty] | Critical |  | Client
DWG-178 |  | Cable schedule & routing layout | [5 empty] | 2026-07-23 | 8 | Consultant | ⚠ SLD rev-3 not approved – panel manufacturing on hold | [6 empty] | Critical |  | Consultant
MAR-066 |  | LED light fitting make & lux calculation | [5 empty] | 2026-07-16 | 15 | Client | ⚠ CEIG drawing submission not started – statutory approval at risk | [6 empty] | High |  | PMC
RFI-094 |  | CEIG drawing submission set & timeline | [5 empty] | 2026-07-29 | 2 | PMC | ⚠ Cable tray route clashes with mechanical piping at Grid B-4 | [6 empty] | Medium |  | Contractor
14. TODAY'S HIGHLIGHTS | [10 empty] | 15. NEXT DAY PLAN
★ 7 nos. earthing pits completed with strip and tested | [10 empty] | ➜ Continue earthing pits – 4 nos. in Bay-2
★ Earth resistance readings of 5 pits all below 2 ohm | [10 empty] | ➜ Cable tray erection in Bay-1 after PEB sheeting clearance
★ Cable tray support fabrication started for Bay-1 | [10 empty] | ➜ Conduit laying in office block slab with civil coordination
★ Panel FAT report for MCC-1 received and under review | [10 empty] | ➜ Follow up SLD rev-3 approval with consultant
16. DECISIONS / INSTRUCTIONS REQUIRED FROM CLIENT / CONSULTANT / VENDOR
1. Release of the transformer order – 14 week lead time will not meet the December charging date
2. Approval of SLD rev-3 (RFI-093) – pending 11 days, LT panel manufacturing cannot start
3. Nomination of the CEIG liaison consultant and drawing submission schedule
Prepared By |  |  |  |  | Checked By |  |  |  |  | Approved By |  |  |  |  | Client Representative
Name / Sign / Date — Site Engineer – SPDC |  |  |  |  | Name / Sign / Date — QA/QC Engineer – SPDC |  |  |  |  | Name / Sign / Date — Project Manager – SPDC |  |  |  |  | Name / Sign / Date — For and on behalf of Client
Sharnam Project Development Consultants & Co. (SPDC), Vadodara ¦ Project Management Consultancy ¦ THIS SHEET IS ALL FORMULAS — enter data on the INPUT sheet ¦ A3 Landscape – Page 1 of 1

## INPUT
DAILY INPUT SHEET — ELECTRICAL WORKS PACKAGE — HT / LT, CABLING, LIGHTING & EARTHING
TYPE ONLY IN THE YELLOW CELLS ON THIS SHEET. The DASHBOARD sheet is the printed DPR — it is all formulas and must not be typed over. Fill top to bottom, then print the DASHBOARD to PDF.
1. PROJECT HEADER (change once at the start, then only the dates each day)
Project name | <Client / Project Name>
Project manager | <PMC Project Manager>
Contractor / vendor | <Executing Agency / PEB Vendor>
Location | <Plot / GIDC / District>
Prepared by | Site Engineer – SPDC (PMC)
Contract / PO reference | <Work Order No. & Date>
Contract completion date | 2026-09-30
Calendar / working hours | 6 Days / Week – 8 hrs |  |  | Shift hours drive man-days & utilization
Shift hours per day | 8 |  |  | Used for man-days and equipment utilization
Weather | Partly Cloudy, 32 °C
REPORT DATE | 2026-07-31
DATA DATE (cut-off) | 2026-07-31 |  |  | Every planned % is measured to this date
Report number | DPR/ELE-027
AC – certified / paid to date (₹ Lakh) | 1.4 |  |  | From the RA bill / cost report
Cumulative man-days upto previous day | 1180
Cumulative safe man-hours upto prev. day | 42150
Date of last LTI | 2026-03-31 |  |  | Days without LTI counts from here
2. QUANTITY PROGRESS (one row per BOQ / scope item — type today's quantity in the last column)
GROUP | DESCRIPTION OF ITEM |  | UNIT | SCOPE / BOQ QTY | RATE ₹ | START | FINISH | CUM QTY UPTO PREV. | QTY TODAY
ELE-10 | HT panel / VCB 11 kV with accessories |  | NOS | 2 | 685000 | 2026-09-01 | 2026-10-10 | 0 | 0
ELE-10 | Transformer 1250 kVA – erection & oil filling |  | NOS | 2 | 1450000 | 2026-09-15 | 2026-10-25 | 0 | 0
ELE-10 | HT cable 11 kV 3C x 240 sqmm laying |  | RM | 320 | 2850 | 2026-09-20 | 2026-10-30 | 0 | 0
ELE-20 | LT main panel (PCC) erection |  | NOS | 1 | 1850000 | 2026-09-25 | 2026-11-05 | 0 | 0
ELE-20 | MCC & distribution boards |  | NOS | 14 | 145000 | 2026-10-01 | 2026-11-15 | 0 | 0
ELE-20 | LT power cable 3.5C x 300 sqmm laying |  | RM | 860 | 1650 | 2026-10-05 | 2026-11-20 | 0 | 0
ELE-20 | Cable tray, ladder & support system |  | RM | 1250 | 780 | 2026-08-15 | 2026-10-20 | 0 | 0
ELE-30 | Internal wiring points – light & power |  | NOS | 640 | 1250 | 2026-09-10 | 2026-11-10 | 0 | 0
ELE-30 | LED high bay, street & flame proof fittings |  | NOS | 186 | 4800 | 2026-10-10 | 2026-11-25 | 0 | 0
ELE-30 | Conduits, raceways & accessories |  | RM | 2400 | 165 | 2026-08-20 | 2026-10-30 | 0 | 0
ELE-40 | Earthing pits with GI / copper strip |  | NOS | 28 | 18500 | 2026-07-15 | 2026-09-10 | 6 | 1
ELE-40 | Lightning protection with air terminals |  | LS | 1 | 385000 | 2026-09-05 | 2026-10-15 | 0 | 0
ELE-50 | Cable termination, glanding & megger test |  | NOS | 320 | 850 | 2026-10-20 | 2026-12-05 | 0 | 0
ELE-50 | Panel testing, relay setting & charging |  | LS | 1 | 480000 | 2026-11-15 | 2026-12-15 | 0 | 0
ELE-50 | CEIG statutory inspection & approval |  | LS | 1 | 275000 | 2026-12-01 | 2026-12-20 | 0 | 0
3. MANPOWER DEPLOYED TODAY
TRADE / CATEGORY |  | PLANNED NOS | ACTUAL NOS | HOURS WORKED
Electrician |  | 10 | 8 | 8.5
Cable Jointer |  | 4 | 2 | 8.5
Fitter – tray & support |  | 6 | 5 | 8.5
Helper |  | 12 | 9 | 8.5
Testing Technician |  | 2 | 1 | 8
Supervisor & PMC Staff |  | 4 | 4 | 9
4. EQUIPMENT DEPLOYED TODAY
EQUIPMENT |  | QTY | WORKED HRS | IDLE HRS
Hydra 8 T |  | 1 | 4 | 4
Cable Drum Stand & Rollers |  | 2 | 6 | 10
Megger / Insulation Tester |  | 2 | 3 | 13
Crimping & Hydraulic Tools |  | 4 | 18 | 14
Drilling & Chasing Machines |  | 6 | 30 | 18
DG Set & Welding Machine |  | 2 | 11 | 5
5. MATERIAL AT SITE
MATERIAL |  | UNIT | OPENING STOCK | RECEIVED TODAY | CONSUMED / ISSUED
Cable tray & ladder – perforated |  | RM | 420 | 120 | 0
Conduits, bends & accessories |  | RM | 680 | 200 | 0
Earthing strip & GI pipe electrodes |  | KGS | 480 | 0 | 68
LT / HT cable (on drums) |  | RM | 0 | 0 | 0
Light fittings – LED high bay |  | NOS | 0 | 0 | 0
Lugs, glands & consumables |  | NOS | 640 | 100 | 46
6. QUALITY CONTROL & TESTS TODAY
QUALITY / TEST PARAMETER |  | TODAY'S FIGURE
Earth pit resistance readings |  | 5 pits, all < 2 ohm
Insulation (megger) test records |  | Not yet due
Cable schedule vs. drawing verification |  | Under review
Panel FAT report received |  | 1 of 3 panels
Earthing strip welding & painting check |  | 6 joints cleared
NCRs open / closed today |  | 0 / 1
7. HSE / SAFETY STATISTICS
HSE PARAMETER |  | TODAY'S FIGURE
Safe man-hours – today / cumulative |  | 250 / 4,320
Days without LTI |  | 122
Electrical work permits issued |  | 3
LOTO applied on live circuits |  | Yes – 2 points
Work at height permits issued |  | 2
Safety observations raised / closed |  | 3 / 3
8. DELAY / IDLE TIME LOG TODAY (enter clock times — hours are calculated)
CAUSE OF DELAY / IDLE TIME |  | CATEGORY | FROM | TO | EOT
Shutdown not granted for HT termination |  | Client / Vendor | 10:00 | 13:00 | Yes
Rain – outdoor earthing work stopped |  | Weather | 15:00 | 16:30 | Review
Cable jointer gang short by 2 nos. |  | Contractor | 8:00 | 9:30 | No
9. DRAWINGS / RFI / MATERIAL APPROVALS PENDING (ageing is calculated)
REF. NO. | DESCRIPTION |  | RAISED ON | PENDING WITH
RFI-093 | Single line diagram rev-3 – approval |  | 2026-07-20 | Consultant
DWG-178 | Cable schedule & routing layout |  | 2026-07-23 | Consultant
MAR-066 | LED light fitting make & lux calculation |  | 2026-07-16 | Client
RFI-094 | CEIG drawing submission set & timeline |  | 2026-07-29 | PMC
10. ISSUES & RISKS (open items)
ISSUE / RISK DESCRIPTION |  |  | SEVERITY | OWNER
Transformer delivery lead time 14 weeks – order not yet released |  |  | Critical | Client
SLD rev-3 not approved – panel manufacturing on hold |  |  | Critical | Consultant
CEIG drawing submission not started – statutory approval at risk |  |  | High | PMC
Cable tray route clashes with mechanical piping at Grid B-4 |  |  | Medium | Contractor
11. TODAY'S HIGHLIGHTS
7 nos. earthing pits completed with strip and tested
Earth resistance readings of 5 pits all below 2 ohm
Cable tray support fabrication started for Bay-1
Panel FAT report for MCC-1 received and under review
12. NEXT DAY PLAN
Continue earthing pits – 4 nos. in Bay-2
Cable tray erection in Bay-1 after PEB sheeting clearance
Conduit laying in office block slab with civil coordination
Follow up SLD rev-3 approval with consultant
13. DECISIONS REQUIRED FROM CLIENT / CONSULTANT / VENDOR
Release of the transformer order – 14 week lead time will not meet the December charging date
Approval of SLD rev-3 (RFI-093) – pending 11 days, LT panel manufacturing cannot start
Nomination of the CEIG liaison consultant and drawing submission schedule
14. S-CURVE ACTUAL HISTORY (enter once per reporting period — today's point is automatic)
DATE | ACTUAL CUM % ON THAT DATE | NOTE
2026-07-01 | 0% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-06 | 0.4005% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-11 | 0.8368% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-16 | 0.8368% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-21 | 0.8368% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-26 | 0.8368% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-31 | ◄ calculated on the DASHBOARD | TODAY — taken from the quantity table, do not type
2026-08-05 |  | leave blank until that date is reported
2026-08-10 |  | leave blank until that date is reported
2026-08-15 |  | leave blank until that date is reported
2026-08-20 |  | leave blank until that date is reported
2026-08-25 |  | leave blank until that date is reported
2026-08-30 |  | leave blank until that date is reported

## S-Curve Calc
S-CURVE CALCULATION — ACTUAL % ON EACH REPORTING DATE (ELECTRICAL)
Enter the CUMULATIVE quantity of each item as it stood on each reporting date (from that day's measurement book / issued DPR). The bottom row converts them into the weighted actual % for that date and feeds INPUT section 14 and the S-curve. Once a column is filled it never changes again.
SL | DESCRIPTION OF ITEM | UNIT | SCOPE QTY | WEIGHT-AGE % | 2026-07-01 | 2026-07-06 | 2026-07-11 | 2026-07-16 | 2026-07-21 | 2026-07-26 | 2026-07-31 | 2026-08-05 | 2026-08-10 | 2026-08-15 | 2026-08-20 | 2026-08-25 | 2026-08-30
1 | HT panel / VCB 11 kV with accessories | NOS | 2 | 8.853% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
2 | Transformer 1250 kVA – erection & oil filling | NOS | 2 | 18.74% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
3 | HT cable 11 kV 3C x 240 sqmm laying | RM | 320 | 5.893% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
4 | LT main panel (PCC) erection | NOS | 1 | 11.95% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
5 | MCC & distribution boards | NOS | 14 | 13.12% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
6 | LT power cable 3.5C x 300 sqmm laying | RM | 860 | 9.17% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
7 | Cable tray, ladder & support system | RM | 1250 | 6.301% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
8 | Internal wiring points – light & power | NOS | 640 | 5.17% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
9 | LED high bay, street & flame proof fittings | NOS | 186 | 5.769% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
10 | Conduits, raceways & accessories | RM | 2400 | 2.559% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
11 | Earthing pits with GI / copper strip | NOS | 28 | 3.347% | 2026-07-01: 0; 2026-07-06: 3.35; 2026-07-11: 7; 2026-07-16: 7; 2026-07-21: 7; 2026-07-26: 7
12 | Lightning protection with air terminals | LS | 1 | 2.488% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
13 | Cable termination, glanding & megger test | NOS | 320 | 1.758% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
14 | Panel testing, relay setting & charging | LS | 1 | 3.102% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
15 | CEIG statutory inspection & approval | LS | 1 | 1.777% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
WEIGHTED ACTUAL % ON THAT DATE |  |  |  | 100% | 0% | 0.4005% | 0.8368% | 0.8368% | 0.8368% | 0.8368% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
FORMULA: Actual % on a date = Σ [ item weightage × ( cumulative qty on that date ÷ scope qty ) ] — the same weighted calculation the DASHBOARD does for today, only using the quantities as they stood on that earlier date.
SHORTCUT: if the DPR was already issued on that date, simply type the Actual % printed on it over the green formula in INPUT section 14 — both routes give the same figure. NOTE: weightage is taken from the CURRENT rates, so if a rate is revised later, re-issued history will shift slightly; the figures on the DPRs already signed remain the record.

## Guide
HOW THIS FILE WORKS — ELECTRICAL DPR
| Two sheets only | INPUT — you type here, top to bottom, yellow cells only. DASHBOARD — the printed DPR, 100% formulas, never typed. Guide — this page.
| Daily routine | Open INPUT → change Report Date and Data Date → enter today's quantities, manpower, equipment, material, quality, HSE, delays, pending approvals, issues, highlights, next-day plan → open DASHBOARD → print to PDF.
| Adding / removing an item | Insert or delete a row inside the quantity block on INPUT and the same row position on DASHBOARD; every formula uses ranges, so totals follow.
| Weightage % | Scope Qty × Rate ÷ Σ(Scope Qty × Rate). Value weightage — always totals 100%.
| Planned % | IF(Data Date ≥ Finish, 100%, IF(Data Date < Start, 0%, (Data Date − Start + 1) ÷ (Finish − Start + 1))) — the programme prorated to the cut-off date.
| Days +/− | Finish − Data Date. Negative and red means the item is already past its programmed finish.
| Cum Qty To Date / Balance | Cum upto previous + Qty today · Scope Qty − Cum to date.
| % Complete | MIN(Cum Qty To Date ÷ Scope Qty, 1), shown with an in-cell data bar.
| Earned ₹ today | Qty today × Rate — the value of work done in the day, totalled in the KPI strip.
| Package Planned / Actual % | Σ(Weightage × Planned %) and Σ(Weightage × % Complete). These two totals drive the KPI strip, group summary, earned value block and S-curve.
| Status | Not Started / Completed / On Track (actual ≥ planned) / In Progress / Delay — colour coded.
| Group summary | SUMIFS of the weighted columns by group code ÷ that group's weightage.
| Earned value | BAC = Σ(Qty × Rate) ÷ 1,00,000 · PV = BAC × Planned % · EV = BAC × Actual % · SV = EV − PV · CV = EV − AC · CPI = EV ÷ AC · EAC = BAC ÷ CPI. Only AC is typed.
| Section 6 / 7 / 8 | Man-days = Actual Nos × hours ÷ shift hours · Utilization = Worked ÷ (Qty × shift hours) · Balance stock = Opening + Received − Consumed.
| Hours lost | (To − From) × 24 from the clock times on INPUT. EOT count is a COUNTIF of the Yes entries.
| Approval ageing | Data Date − Raised on; red beyond 7 days, and counted in the Project Health box.
| S-curve actual history | Actual % on any past date = Σ [ item weightage × (cumulative qty on that date ÷ scope qty) ]. The S-CURVE CALC sheet does this for you — enter each item's cumulative quantity as it stood on each reporting date and the bottom row gives the %, which flows into INPUT section 14. If that day's DPR was already issued, just type the Actual % from it instead.
| S-curve | Planned line = SUMPRODUCT of every item's weightage × its time-prorated fraction at each date — built entirely from the programme. Actual history comes from INPUT section 14; today's point is taken live from the quantity table.
| Paper | DASHBOARD is set to A3 landscape, fit to one page. Prints on A4 at about 70% if needed.
| Roll over to the next day | Save a copy with the new date. On INPUT: move Cum Qty To Date into 'Cum qty upto prev.', move material Balance into Opening, clear Qty Today, update the cumulative man-days and man-hours.