## DASHBOARD
SPDC |  |  | DAILY PROGRESS REPORT | [10 empty] | Report Date |  |  | 2026-07-31
[14 empty] | Data Date |  |  | 2026-07-31
|  |  | FIRE FIGHTING & PROTECTION PACKAGE | [10 empty] | Report No. / Day |  |  | DPR/FIR-027 ¦ Friday | [5 empty] | S-CURVE DATA (not printed)
Project Name |  | <Client / Project Name> | [5 empty] | Contract / PO Ref. |  | <Work Order No. & Date> |  |  |  | PROJECT HEALTH | [8 empty] | DATE | PLANNED CUM % | ACTUAL CUM % | NOTE
Project Manager |  | <PMC Project Manager> | [5 empty] | Contract Completion |  | 2026-09-30 |  |  |  | Overall Status |  |  |  | BEHIND PROGRAMME |  |  |  |  | 2026-07-01 | 0% | 0% | from INPUT sheet section 14
Contractor / Vendor |  | <Executing Agency / PEB Vendor> | [5 empty] | Calendar / Weather |  | 6 Days / Week – 8 hrs ¦ Partly Cloudy, 32 °C |  |  |  | Critical / High issues open |  |  |  | 3 |  |  |  |  | 2026-07-06 | 0.5232% | 0.7997% | from INPUT sheet section 14
Location |  | <Plot / GIDC / District> | [5 empty] | Contract Value (₹ Lakh) |  | 143.47 |  |  |  | Approvals pending > 7 days |  |  |  | 2 |  |  |  |  | 2026-07-11 | 1.831% | 2.1% | from INPUT sheet section 14
1. KEY PERFORMANCE INDICATORS (all calculated — nothing is typed on this sheet) | [22 empty] | 2026-07-16 | 3.286% | 3.799% | from INPUT sheet section 14
PLANNED % |  |  | ACTUAL % |  |  | VARIANCE |  |  | SPI |  |  | EARNED VALUE ₹ L |  |  | VALUE DONE TODAY ₹ |  |  | ITEMS DELAYED |  | HRS LOST TODAY |  |  | 2026-07-21 | 4.74% | 5.079% | from INPUT sheet section 14
8.18% |  |  | 5.079% |  |  | -3.101% |  |  | 0.62089 |  |  | 7.287 |  |  | 93400 |  |  | 1 |  | 5.5 |  |  | 2026-07-26 | 6.347% | 5.079% | from INPUT sheet section 14
2. QUANTITY / PHYSICAL PROGRESS — ITEM-WISE (basis of the % complete above) | [22 empty] | 2026-07-31 | 8.18% | 5.079% | ◄ today – from the quantity table
SL | DESCRIPTION OF ITEM |  |  |  | UNIT | SCOPE QTY | RATE ₹ | WEIGHT-AGE % | START | FINISH | DAYS +/− | PLANNED % | CUM QTY PREV. | QTY TODAY | CUM QTY TO DATE | BALANCE QTY | % COMPL. | EARNED ₹ TODAY | WTD. PLANNED % | WTD. ACTUAL % | STATUS |  | 2026-08-05 | 11.17% |  | from INPUT sheet section 14
1 | Excavation & laying of UG MS pipe 150 NB |  |  |  | RM | 720 | 2450 | 12.3% | 2026-07-05 | 2026-08-20 | 20 | 57.45% | 210 | 24 | 234 | 486 | 32.5% | 58800 | 7.063% | 3.996% | Delay | FIR-10 | 2026-08-10 | 14.15% |  | from INPUT sheet section 14
2 | Yard hydrant valves with hose box & monitor |  |  |  | NOS | 18 | 26000 | 3.262% | 2026-07-25 | 2026-09-05 | 36 | 16.28% | 2 | 1 | 3 | 15 | 16.67% | 26000 | 0.531% | 0.5437% | On Track | FIR-10 | 2026-08-15 | 17.14% |  | from INPUT sheet section 14
3 | Thrust blocks, chambers & anticorrosive taping |  |  |  | NOS | 22 | 8600 | 1.319% | 2026-07-12 | 2026-08-25 | 25 | 44.44% | 8 | 1 | 9 | 13 | 40.91% | 8600 | 0.5861% | 0.5395% | In Progress | FIR-10 | 2026-08-20 | 20.25% |  | from INPUT sheet section 14
4 | Fire water storage tank – 250 KL |  |  |  | LS | 1 | 1850000 | 12.89% | 2026-08-01 | 2026-09-25 | 56 | 0% | 0 | 0 | 0 | 1 | 0% | 0 | 0% | 0% | Not Started | FIR-20 | 2026-08-25 | 22.59% |  | from INPUT sheet section 14
5 | Fire pumps – electric, diesel & jockey set |  |  |  | SET | 1 | 2650000 | 18.47% | 2026-09-01 | 2026-10-10 | 71 | 0% | 0 | 0 | 0 | 1 | 0% | 0 | 0% | 0% | Not Started | FIR-20 | 2026-08-30 | 24.78% |  | from INPUT sheet section 14
6 | Pump house piping, headers & valves |  |  |  | MT | 8 | 145000 | 8.085% | 2026-09-10 | 2026-10-20 | 81 | 0% | 0 | 0 | 0 | 8 | 0% | 0 | 0% | 0% | Not Started | FIR-20
7 | Internal hydrant riser & piping 100 NB |  |  |  | RM | 480 | 1850 | 6.189% | 2026-08-20 | 2026-10-05 | 66 | 0% | 0 | 0 | 0 | 480 | 0% | 0 | 0% | 0% | Not Started | FIR-30
8 | Sprinkler piping 25 to 80 NB |  |  |  | RM | 1650 | 980 | 11.27% | 2026-09-01 | 2026-10-25 | 86 | 0% | 0 | 0 | 0 | 1650 | 0% | 0 | 0% | 0% | Not Started | FIR-30
9 | Sprinkler heads & flow / tamper switches |  |  |  | NOS | 720 | 780 | 3.914% | 2026-09-20 | 2026-11-05 | 97 | 0% | 0 | 0 | 0 | 720 | 0% | 0 | 0% | 0% | Not Started | FIR-30
10 | Landing valves, hose reel & cabinets |  |  |  | NOS | 24 | 18500 | 3.095% | 2026-10-01 | 2026-11-10 | 102 | 0% | 0 | 0 | 0 | 24 | 0% | 0 | 0% | 0% | Not Started | FIR-30
11 | Fire alarm panel & repeater panel |  |  |  | NOS | 2 | 285000 | 3.973% | 2026-10-05 | 2026-11-15 | 107 | 0% | 0 | 0 | 0 | 2 | 0% | 0 | 0% | 0% | Not Started | FIR-40
12 | Detectors, MCP & hooters with wiring |  |  |  | NOS | 260 | 3200 | 5.799% | 2026-10-10 | 2026-11-25 | 117 | 0% | 0 | 0 | 0 | 260 | 0% | 0 | 0% | 0% | Not Started | FIR-40
13 | Portable extinguishers – ABC / CO2 |  |  |  | NOS | 86 | 4200 | 2.518% | 2026-11-01 | 2026-11-20 | 112 | 0% | 0 | 0 | 0 | 86 | 0% | 0 | 0% | 0% | Not Started | FIR-50
14 | Hydro testing & flushing of network |  |  |  | RM | 2850 | 120 | 2.384% | 2026-10-15 | 2026-11-30 | 122 | 0% | 0 | 0 | 0 | 2850 | 0% | 0 | 0% | 0% | Not Started | FIR-50
15 | Commissioning, third party & statutory approval |  |  |  | LS | 1 | 650000 | 4.531% | 2026-11-20 | 2026-12-15 | 137 | 0% | 0 | 0 | 0 | 1 | 0% | 0 | 0% | 0% | Not Started | FIR-50
TOTAL / OVERALL PACKAGE PROGRESS |  |  |  |  | ₹ 143.5 Lakh |  |  | 100% | PROGRAMME |  |  | 8.18% |  |  |  |  | 5.079% | 93400 | 8.18% | 5.079% | BEHIND
3. PROGRESS SUMMARY BY GROUP (value weighted) | [9 empty] | 4. PROGRESS S-CURVE (PLANNED vs ACTUAL)
GROUP |  | DESCRIPTION |  |  | WEIGHTAGE |  | PLANNED % | ACTUAL % | SPI
FIR-10 |  | Underground & Yard Hydrant Network |  |  | 16.88% |  | 48.47% | 30.1% | 0.62089
FIR-20 |  | Pump House, Fire Water Tank & Headers |  |  | 39.45% |  | 0% | 0%
FIR-30 |  | Internal Hydrant, Sprinkler & Piping |  |  | 24.47% |  | 0% | 0%
FIR-40 |  | Fire Alarm & Detection System |  |  | 9.772% |  | 0% | 0%
FIR-50 |  | Extinguishers, Testing & Statutory Approval |  |  | 9.432% |  | 0% | 0%
TOTAL |  |  |  |  | 100% |  | 8.18% | 5.079% | 0.62089
5. EARNED VALUE / COMMERCIAL SNAPSHOT (₹ in Lakh)
BAC – Contract value of package | [6 empty] | 143.47
PV – Planned Value (BAC × Planned %) | [6 empty] | 11.7364
EV – Earned Value (BAC × Actual %) | [6 empty] | 7.287
AC – Certified / paid to date | [6 empty] | 7.7
SV – Schedule Variance (EV − PV) | [6 empty] | -4.4494
CV – Cost Variance (EV − AC) | [6 empty] | -0.413
CPI ¦ EAC (BAC ÷ CPI) | [6 empty] | 0.95 ¦ ₹ 151.6 L
6. MANPOWER DEPLOYED TODAY | [6 empty] | 7. EQUIPMENT UTILIZATION TODAY | [6 empty] | 8. KEY MATERIAL AT SITE
TRADE / CATEGORY |  |  | PLAN | ACTUAL | MAN-DAYS |  | EQUIPMENT |  |  | QTY | WORKED HRS | IDLE HRS | UTIL. % | MATERIAL |  |  | UNIT | OPENING | RECD. | CONSUMED | BALANCE
Fire Fitter / Pipe Fitter |  |  | 10 | 8 | 8.5 |  | Excavator – JCB 3DX |  |  | 1 | 6 | 2 | 75% | MS Pipe 150 NB (UG network) |  |  | RM | 380 | 60 | 24 | 416
Welder |  |  | 6 | 5 | 5.3125 |  | Hydra 8 T |  |  | 1 | 4.5 | 3.5 | 56.25% | MS / GI Pipe 25 to 100 NB |  |  | RM | 240 | 0 | 0 | 240
Mason – chambers & thrust blocks |  |  | 4 | 4 | 4 |  | Welding Machine 400 A |  |  | 4 | 26 | 6 | 81.25% | Hydrant valves, hose & couplings |  |  | NOS | 12 | 4 | 1 | 15
Helper |  |  | 12 | 10 | 10.625 |  | Pipe Threading & Grooving M/C |  |  | 2 | 10 | 6 | 62.5% | Sprinkler heads & flow switches |  |  | NOS | 0 | 0 | 0 | 0
Machine Operator |  |  | 3 | 2 | 2 |  | Hydro Test Pump |  |  | 1 | 3 | 5 | 37.5% | Anticorrosive tape, primer & paint |  |  | LTR | 180 | 40 | 26 | 194
Supervisor & PMC Staff |  |  | 4 | 4 | 4.5 |  | DG Set & De-watering Pump |  |  | 2 | 12 | 4 | 75% | Fittings, flanges & fasteners |  |  | NOS | 460 | 60 | 48 | 472
TOTAL WORKERS / MAN-DAYS |  |  | 39 | 33 | 34.9375 |  | TOTAL / AVERAGE |  |  | 11 | 61.5 | 26.5 | 69.89% | Balance = Opening + Received − Consumed · carry Balance forward as tomorrow's Opening on the INPUT sheet
9. QUALITY CONTROL & TESTS TODAY | [6 empty] | 10. HSE / SAFETY STATISTICS | [6 empty] | 11. DELAY / IDLE TIME LOG TODAY
UG pipe joint weld visual |  |  |  |  | 18 offered, 17 cleared |  | Safe man-hours – today / cumulative |  |  |  |  | 280 / 6,420 |  | CAUSE (CATEGORY) |  |  |  | FROM | TO | HRS LOST | EOT
Hydro test – 12 kg/cm² for 2 hrs |  |  |  |  | Section-1 passed |  | Days without LTI |  |  |  |  | 122 |  | Rain – trench flooded, laying stopped (Weather) |  |  |  | 14:00 | 16:30 | 2.5 | Review
Anticorrosive taping – holiday test |  |  |  |  | 3 stretches, all OK |  | Excavation permits issued |  |  |  |  | 2 |  | Hydrant valve consignment not received (Client / Vendor) |  |  |  | 10:00 | 12:00 | 2 | Yes
Trench bedding & backfill compaction |  |  |  |  | 2 tests taken |  | Hot work permits issued |  |  |  |  | 3 |  | Road crossing permission awaited (Statutory) |  |  |  | 8:30 | 9:30 | 1 | Yes
Third party / TAC inspection status |  |  |  |  | Not yet due |  | Trench barricading & signage verified |  |  |  |  | Yes – full length | [5 empty] | 0:00 | 0:00 |  | 0
NCRs open / closed today |  |  |  |  | 1 / 0 |  | Safety observations raised / closed |  |  |  |  | 4 / 4 |  | TOTAL HOURS LOST TODAY | [5 empty] | 5.5 | 2 EOT
12. DRAWINGS / RFI / MATERIAL APPROVALS PENDING | [10 empty] | 13. ISSUES & RISKS (open items)
REF. NO. |  | DESCRIPTION | [5 empty] | RAISED ON | AGEING | PENDING WITH | ISSUE / RISK DESCRIPTION | [6 empty] | SEVERITY |  | OWNER
RFI-071 |  | Sprinkler layout as per TAC / NBC – approval | [5 empty] | 2026-07-18 | 13 | Consultant | ⚠ TAC / statutory approval of sprinkler layout pending – holds all internal piping | [6 empty] | Critical |  | Client
DWG-152 |  | Pump house GA & foundation drawing | [5 empty] | 2026-07-24 | 7 | Consultant | ⚠ Fire pump set delivery lead time 12 weeks – order not yet placed | [6 empty] | Critical |  | Client
MAR-058 |  | Sprinkler head & flow switch make approval | [5 empty] | 2026-07-20 | 11 | Client | ⚠ Fire water tank front to be released by civil by 01-Aug | [6 empty] | High |  | Contractor
RFI-072 |  | UG hydrant network road crossing detail | [5 empty] | 2026-07-29 | 2 | PMC | ⚠ Hydrant valve consignment short by 6 nos. | [6 empty] | Medium |  | Contractor
14. TODAY'S HIGHLIGHTS | [10 empty] | 15. NEXT DAY PLAN
★ UG MS 150 NB pipe laid & welded – 234 RM of 720 RM | [10 empty] | ➜ Continue UG pipe laying – Chainage 240 to 300
★ Hydro test of Section-1 (0 to 120 RM) passed at 12 kg/cm² | [10 empty] | ➜ Backfilling of tested section after PMC clearance
★ 8 nos. thrust blocks and 3 valve chambers completed | [10 empty] | ➜ Fixing of 2 nos. yard hydrant valves with hose box
★ Anticorrosive taping completed for 180 RM | [10 empty] | ➜ Follow up hydrant valve balance consignment
16. DECISIONS / INSTRUCTIONS REQUIRED FROM CLIENT / CONSULTANT / VENDOR
1. TAC / statutory approval of the sprinkler layout (RFI-071) – pending 13 days, all internal fire piping is held
2. Placement of the fire pump set order – 12 week lead time will not meet the December commissioning date
3. Release of the fire water tank foundation front by the civil agency – required by 01-Aug-26
Prepared By |  |  |  |  | Checked By |  |  |  |  | Approved By |  |  |  |  | Client Representative
Name / Sign / Date — Site Engineer – SPDC |  |  |  |  | Name / Sign / Date — QA/QC Engineer – SPDC |  |  |  |  | Name / Sign / Date — Project Manager – SPDC |  |  |  |  | Name / Sign / Date — For and on behalf of Client
Sharnam Project Development Consultants & Co. (SPDC), Vadodara ¦ Project Management Consultancy ¦ THIS SHEET IS ALL FORMULAS — enter data on the INPUT sheet ¦ A3 Landscape – Page 1 of 1

## INPUT
DAILY INPUT SHEET — FIRE FIGHTING & PROTECTION PACKAGE
TYPE ONLY IN THE YELLOW CELLS ON THIS SHEET. The DASHBOARD sheet is the printed DPR — it is all formulas and must not be typed over. Fill top to bottom, then print the DASHBOARD to PDF.
1. PROJECT HEADER (change once at the start, then only the dates each day)
Project name | <Client / Project Name>
Project manager | <PMC Project Manager>
Contractor / vendor | <Executing Agency / PEB Vendor>
Location | <Plot / GIDC / District>
Prepared by | Site Engineer – SPDC (PMC)
Contract / PO reference | <Work Order No. & Date>
Contract completion date | 2026-09-30
Calendar / working hours | 6 Days / Week – 8 hrs |  |  | Shift hours drive man-days & utilization
Shift hours per day | 8 |  |  | Used for man-days and equipment utilization
Weather | Partly Cloudy, 32 °C
REPORT DATE | 2026-07-31
DATA DATE (cut-off) | 2026-07-31 |  |  | Every planned % is measured to this date
Report number | DPR/FIR-027
AC – certified / paid to date (₹ Lakh) | 7.7 |  |  | From the RA bill / cost report
Cumulative man-days upto previous day | 1180
Cumulative safe man-hours upto prev. day | 42150
Date of last LTI | 2026-03-31 |  |  | Days without LTI counts from here
2. QUANTITY PROGRESS (one row per BOQ / scope item — type today's quantity in the last column)
GROUP | DESCRIPTION OF ITEM |  | UNIT | SCOPE / BOQ QTY | RATE ₹ | START | FINISH | CUM QTY UPTO PREV. | QTY TODAY
FIR-10 | Excavation & laying of UG MS pipe 150 NB |  | RM | 720 | 2450 | 2026-07-05 | 2026-08-20 | 210 | 24
FIR-10 | Yard hydrant valves with hose box & monitor |  | NOS | 18 | 26000 | 2026-07-25 | 2026-09-05 | 2 | 1
FIR-10 | Thrust blocks, chambers & anticorrosive taping |  | NOS | 22 | 8600 | 2026-07-12 | 2026-08-25 | 8 | 1
FIR-20 | Fire water storage tank – 250 KL |  | LS | 1 | 1850000 | 2026-08-01 | 2026-09-25 | 0 | 0
FIR-20 | Fire pumps – electric, diesel & jockey set |  | SET | 1 | 2650000 | 2026-09-01 | 2026-10-10 | 0 | 0
FIR-20 | Pump house piping, headers & valves |  | MT | 8 | 145000 | 2026-09-10 | 2026-10-20 | 0 | 0
FIR-30 | Internal hydrant riser & piping 100 NB |  | RM | 480 | 1850 | 2026-08-20 | 2026-10-05 | 0 | 0
FIR-30 | Sprinkler piping 25 to 80 NB |  | RM | 1650 | 980 | 2026-09-01 | 2026-10-25 | 0 | 0
FIR-30 | Sprinkler heads & flow / tamper switches |  | NOS | 720 | 780 | 2026-09-20 | 2026-11-05 | 0 | 0
FIR-30 | Landing valves, hose reel & cabinets |  | NOS | 24 | 18500 | 2026-10-01 | 2026-11-10 | 0 | 0
FIR-40 | Fire alarm panel & repeater panel |  | NOS | 2 | 285000 | 2026-10-05 | 2026-11-15 | 0 | 0
FIR-40 | Detectors, MCP & hooters with wiring |  | NOS | 260 | 3200 | 2026-10-10 | 2026-11-25 | 0 | 0
FIR-50 | Portable extinguishers – ABC / CO2 |  | NOS | 86 | 4200 | 2026-11-01 | 2026-11-20 | 0 | 0
FIR-50 | Hydro testing & flushing of network |  | RM | 2850 | 120 | 2026-10-15 | 2026-11-30 | 0 | 0
FIR-50 | Commissioning, third party & statutory approval |  | LS | 1 | 650000 | 2026-11-20 | 2026-12-15 | 0 | 0
3. MANPOWER DEPLOYED TODAY
TRADE / CATEGORY |  | PLANNED NOS | ACTUAL NOS | HOURS WORKED
Fire Fitter / Pipe Fitter |  | 10 | 8 | 8.5
Welder |  | 6 | 5 | 8.5
Mason – chambers & thrust blocks |  | 4 | 4 | 8
Helper |  | 12 | 10 | 8.5
Machine Operator |  | 3 | 2 | 8
Supervisor & PMC Staff |  | 4 | 4 | 9
4. EQUIPMENT DEPLOYED TODAY
EQUIPMENT |  | QTY | WORKED HRS | IDLE HRS
Excavator – JCB 3DX |  | 1 | 6 | 2
Hydra 8 T |  | 1 | 4.5 | 3.5
Welding Machine 400 A |  | 4 | 26 | 6
Pipe Threading & Grooving M/C |  | 2 | 10 | 6
Hydro Test Pump |  | 1 | 3 | 5
DG Set & De-watering Pump |  | 2 | 12 | 4
5. MATERIAL AT SITE
MATERIAL |  | UNIT | OPENING STOCK | RECEIVED TODAY | CONSUMED / ISSUED
MS Pipe 150 NB (UG network) |  | RM | 380 | 60 | 24
MS / GI Pipe 25 to 100 NB |  | RM | 240 | 0 | 0
Hydrant valves, hose & couplings |  | NOS | 12 | 4 | 1
Sprinkler heads & flow switches |  | NOS | 0 | 0 | 0
Anticorrosive tape, primer & paint |  | LTR | 180 | 40 | 26
Fittings, flanges & fasteners |  | NOS | 460 | 60 | 48
6. QUALITY CONTROL & TESTS TODAY
QUALITY / TEST PARAMETER |  | TODAY'S FIGURE
UG pipe joint weld visual |  | 18 offered, 17 cleared
Hydro test – 12 kg/cm² for 2 hrs |  | Section-1 passed
Anticorrosive taping – holiday test |  | 3 stretches, all OK
Trench bedding & backfill compaction |  | 2 tests taken
Third party / TAC inspection status |  | Not yet due
NCRs open / closed today |  | 1 / 0
7. HSE / SAFETY STATISTICS
HSE PARAMETER |  | TODAY'S FIGURE
Safe man-hours – today / cumulative |  | 280 / 6,420
Days without LTI |  | 122
Excavation permits issued |  | 2
Hot work permits issued |  | 3
Trench barricading & signage verified |  | Yes – full length
Safety observations raised / closed |  | 4 / 4
8. DELAY / IDLE TIME LOG TODAY (enter clock times — hours are calculated)
CAUSE OF DELAY / IDLE TIME |  | CATEGORY | FROM | TO | EOT
Rain – trench flooded, laying stopped |  | Weather | 14:00 | 16:30 | Review
Hydrant valve consignment not received |  | Client / Vendor | 10:00 | 12:00 | Yes
Road crossing permission awaited |  | Statutory | 8:30 | 9:30 | Yes
9. DRAWINGS / RFI / MATERIAL APPROVALS PENDING (ageing is calculated)
REF. NO. | DESCRIPTION |  | RAISED ON | PENDING WITH
RFI-071 | Sprinkler layout as per TAC / NBC – approval |  | 2026-07-18 | Consultant
DWG-152 | Pump house GA & foundation drawing |  | 2026-07-24 | Consultant
MAR-058 | Sprinkler head & flow switch make approval |  | 2026-07-20 | Client
RFI-072 | UG hydrant network road crossing detail |  | 2026-07-29 | PMC
10. ISSUES & RISKS (open items)
ISSUE / RISK DESCRIPTION |  |  | SEVERITY | OWNER
TAC / statutory approval of sprinkler layout pending – holds all internal piping |  |  | Critical | Client
Fire pump set delivery lead time 12 weeks – order not yet placed |  |  | Critical | Client
Fire water tank front to be released by civil by 01-Aug |  |  | High | Contractor
Hydrant valve consignment short by 6 nos. |  |  | Medium | Contractor
11. TODAY'S HIGHLIGHTS
UG MS 150 NB pipe laid & welded – 234 RM of 720 RM
Hydro test of Section-1 (0 to 120 RM) passed at 12 kg/cm²
8 nos. thrust blocks and 3 valve chambers completed
Anticorrosive taping completed for 180 RM
12. NEXT DAY PLAN
Continue UG pipe laying – Chainage 240 to 300
Backfilling of tested section after PMC clearance
Fixing of 2 nos. yard hydrant valves with hose box
Follow up hydrant valve balance consignment
13. DECISIONS REQUIRED FROM CLIENT / CONSULTANT / VENDOR
TAC / statutory approval of the sprinkler layout (RFI-071) – pending 13 days, all internal fire piping is held
Placement of the fire pump set order – 12 week lead time will not meet the December commissioning date
Release of the fire water tank foundation front by the civil agency – required by 01-Aug-26
14. S-CURVE ACTUAL HISTORY (enter once per reporting period — today's point is automatic)
DATE | ACTUAL CUM % ON THAT DATE | NOTE
2026-07-01 | 0% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-06 | 0.7997% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-11 | 2.1% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-16 | 3.799% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-21 | 5.079% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-26 | 5.079% | calculated on the S-CURVE CALC sheet — or type the % printed on that day's issued DPR
2026-07-31 | ◄ calculated on the DASHBOARD | TODAY — taken from the quantity table, do not type
2026-08-05 |  | leave blank until that date is reported
2026-08-10 |  | leave blank until that date is reported
2026-08-15 |  | leave blank until that date is reported
2026-08-20 |  | leave blank until that date is reported
2026-08-25 |  | leave blank until that date is reported
2026-08-30 |  | leave blank until that date is reported

## S-Curve Calc
S-CURVE CALCULATION — ACTUAL % ON EACH REPORTING DATE (FIRE FIGHTING)
Enter the CUMULATIVE quantity of each item as it stood on each reporting date (from that day's measurement book / issued DPR). The bottom row converts them into the weighted actual % for that date and feeds INPUT section 14 and the S-curve. Once a column is filled it never changes again.
SL | DESCRIPTION OF ITEM | UNIT | SCOPE QTY | WEIGHT-AGE % | 2026-07-01 | 2026-07-06 | 2026-07-11 | 2026-07-16 | 2026-07-21 | 2026-07-26 | 2026-07-31 | 2026-08-05 | 2026-08-10 | 2026-08-15 | 2026-08-20 | 2026-08-25 | 2026-08-30
1 | Excavation & laying of UG MS pipe 150 NB | RM | 720 | 12.3% | 2026-07-01: 0; 2026-07-06: 36.86; 2026-07-11: 96.75; 2026-07-16: 175.07; 2026-07-21: 234; 2026-07-26: 234
2 | Yard hydrant valves with hose box & monitor | NOS | 18 | 3.262% | 2026-07-01: 0; 2026-07-06: 0.47; 2026-07-11: 1.24; 2026-07-16: 2.24; 2026-07-21: 3; 2026-07-26: 3
3 | Thrust blocks, chambers & anticorrosive taping | NOS | 22 | 1.319% | 2026-07-01: 0; 2026-07-06: 1.42; 2026-07-11: 3.72; 2026-07-16: 6.73; 2026-07-21: 9; 2026-07-26: 9
4 | Fire water storage tank – 250 KL | LS | 1 | 12.89% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
5 | Fire pumps – electric, diesel & jockey set | SET | 1 | 18.47% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
6 | Pump house piping, headers & valves | MT | 8 | 8.085% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
7 | Internal hydrant riser & piping 100 NB | RM | 480 | 6.189% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
8 | Sprinkler piping 25 to 80 NB | RM | 1650 | 11.27% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
9 | Sprinkler heads & flow / tamper switches | NOS | 720 | 3.914% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
10 | Landing valves, hose reel & cabinets | NOS | 24 | 3.095% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
11 | Fire alarm panel & repeater panel | NOS | 2 | 3.973% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
12 | Detectors, MCP & hooters with wiring | NOS | 260 | 5.799% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
13 | Portable extinguishers – ABC / CO2 | NOS | 86 | 2.518% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
14 | Hydro testing & flushing of network | RM | 2850 | 2.384% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
15 | Commissioning, third party & statutory approval | LS | 1 | 4.531% | 2026-07-01: 0; 2026-07-06: 0; 2026-07-11: 0; 2026-07-16: 0; 2026-07-21: 0; 2026-07-26: 0
WEIGHTED ACTUAL % ON THAT DATE |  |  |  | 100% | 0% | 0.7997% | 2.1% | 3.799% | 5.079% | 5.079% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
FORMULA: Actual % on a date = Σ [ item weightage × ( cumulative qty on that date ÷ scope qty ) ] — the same weighted calculation the DASHBOARD does for today, only using the quantities as they stood on that earlier date.
SHORTCUT: if the DPR was already issued on that date, simply type the Actual % printed on it over the green formula in INPUT section 14 — both routes give the same figure. NOTE: weightage is taken from the CURRENT rates, so if a rate is revised later, re-issued history will shift slightly; the figures on the DPRs already signed remain the record.

## Guide
HOW THIS FILE WORKS — FIRE FIGHTING DPR
| Two sheets only | INPUT — you type here, top to bottom, yellow cells only. DASHBOARD — the printed DPR, 100% formulas, never typed. Guide — this page.
| Daily routine | Open INPUT → change Report Date and Data Date → enter today's quantities, manpower, equipment, material, quality, HSE, delays, pending approvals, issues, highlights, next-day plan → open DASHBOARD → print to PDF.
| Adding / removing an item | Insert or delete a row inside the quantity block on INPUT and the same row position on DASHBOARD; every formula uses ranges, so totals follow.
| Weightage % | Scope Qty × Rate ÷ Σ(Scope Qty × Rate). Value weightage — always totals 100%.
| Planned % | IF(Data Date ≥ Finish, 100%, IF(Data Date < Start, 0%, (Data Date − Start + 1) ÷ (Finish − Start + 1))) — the programme prorated to the cut-off date.
| Days +/− | Finish − Data Date. Negative and red means the item is already past its programmed finish.
| Cum Qty To Date / Balance | Cum upto previous + Qty today · Scope Qty − Cum to date.
| % Complete | MIN(Cum Qty To Date ÷ Scope Qty, 1), shown with an in-cell data bar.
| Earned ₹ today | Qty today × Rate — the value of work done in the day, totalled in the KPI strip.
| Package Planned / Actual % | Σ(Weightage × Planned %) and Σ(Weightage × % Complete). These two totals drive the KPI strip, group summary, earned value block and S-curve.
| Status | Not Started / Completed / On Track (actual ≥ planned) / In Progress / Delay — colour coded.
| Group summary | SUMIFS of the weighted columns by group code ÷ that group's weightage.
| Earned value | BAC = Σ(Qty × Rate) ÷ 1,00,000 · PV = BAC × Planned % · EV = BAC × Actual % · SV = EV − PV · CV = EV − AC · CPI = EV ÷ AC · EAC = BAC ÷ CPI. Only AC is typed.
| Section 6 / 7 / 8 | Man-days = Actual Nos × hours ÷ shift hours · Utilization = Worked ÷ (Qty × shift hours) · Balance stock = Opening + Received − Consumed.
| Hours lost | (To − From) × 24 from the clock times on INPUT. EOT count is a COUNTIF of the Yes entries.
| Approval ageing | Data Date − Raised on; red beyond 7 days, and counted in the Project Health box.
| S-curve actual history | Actual % on any past date = Σ [ item weightage × (cumulative qty on that date ÷ scope qty) ]. The S-CURVE CALC sheet does this for you — enter each item's cumulative quantity as it stood on each reporting date and the bottom row gives the %, which flows into INPUT section 14. If that day's DPR was already issued, just type the Actual % from it instead.
| S-curve | Planned line = SUMPRODUCT of every item's weightage × its time-prorated fraction at each date — built entirely from the programme. Actual history comes from INPUT section 14; today's point is taken live from the quantity table.
| Paper | DASHBOARD is set to A3 landscape, fit to one page. Prints on A4 at about 70% if needed.
| Roll over to the next day | Save a copy with the new date. On INPUT: move Cum Qty To Date into 'Cum qty upto prev.', move material Balance into Opening, clear Qty Today, update the cumulative man-days and man-hours.