## DASHBOARD
SITE DOCUMENT AUDIT — SCORE
Calculates from FOLDER_SAMPLE and SITE_WALK. Nothing to maintain on this tab.
Project: ______________ Audit ref: __________ Date: __________ Auditor: ______________
FOLDERS |  | WALK CHECKS |  | SCORED | NOT MET | OVERALL SCORE | CRITICAL FINDINGS
FOLDER SCORE |  | SITE WALK SCORE |  | FINDINGS RAISED | FINDINGS OPEN | VERDICT
SITE WALK — SCORE BY SECTION
Section | Checks | Met | Not met | Score
1. SITE OFFICE — DRAWING CONTROL | 5
2. WORKFACE — DRAWINGS AND METHOD | 5
3. WORKFACE — PERMITS AND SAFETY | 6
4. QUALITY AT THE WORKFACE | 6
5. INDUSTRIAL WORKFACE | 6
6. STORES AND MATERIAL | 6
7. HSE AND WELFARE | 5
8. DOCUMENT CONTROL PHYSICAL | 5
VERDICT RULE
PASS | 90% or above, and no Critical finding raised
PASS WITH ACTIONS | 75% to 89%, and no Critical finding raised
FAIL | Below 75%, or any Critical finding raised
A superseded print in use, a pour without written permission, or a permit issued without workface verification is a Critical finding on its own. One of those fails the audit.

## PLAN
SITE DOCUMENT AUDIT — PLAN AND METHOD
SHARANAM PROJECT DEVELOPMENT CONSULTANTS & CO. ¦ One full day on a live industrial site
Audit ref.
Project
Date
Auditor
Independent of this project
Document Controller
Project Manager
BEFORE YOU GO — the desk review
When | Do this | Why it matters | Done | Notes
7 days before | Notify the audit WINDOW, not the exact day | An announced date produces a tidied site office for one day, not a true picture
2 days before | Run the KPI refresh yourself on the master workbook | You see the real numbers, not the ones prepared for you
2 days before | Read the last six weekly reports and the last MPR | Most findings are visible in the data before you reach site
2 days before | Filter 03_SUBJECT_DATA by RAG = RED and by overdue | This is your priority sampling list — go where the system is already failing
2 days before | Check the refresh timestamps for the last six weeks | Gaps tell you the weekly routine is not being run
1 day before | Note which registers are above 80% capacity | A register about to overflow will stop counting silently
1 day before | Print the SITE_WALK and FOLDER_SAMPLE tabs | Do not audit from a laptop while walking the site
WHAT TO TAKE
• | Printed SITE_WALK and FOLDER_SAMPLE sheets
• | The RED and overdue list from the desk review
• | Camera or phone — every finding needs a photograph
• | Safety boots, helmet, hi-vis, glasses. You will be at the workface, not in the office
• | A copy of the current drawing register, so you can check boards against it independently
THE DAY — timetable
Time | Activity | What you are actually testing | Sheet | Done
08:30 | Opening meeting with PM and Document Controller | State scope, criteria and finish time. Ask for nothing in advance — you have already pulled the data | PLAN
08:45 | Document Controller interview | How the system runs in practice, and what slips under pressure. The answers direct your sampling | DC_INTERVIEW
09:30 | Site office inspection — drawing boards and registers | Superseded prints, uncontrolled copies, registers maintained daily or in bursts | SITE_WALK 1, 8
10:15 | Workface walk — drawings, method, permits | Current revisions at the workface, live permits verified, method briefed | SITE_WALK 2, 3
11:15 | Workface walk — quality and industrial controls | Pour cards signed before pour, weld IDs against the log, NDT markings, permits to load | SITE_WALK 4, 5
12:15 | Stores and material | Approved brands, GRNs, test certificates, segregation of rejected material | SITE_WALK 6
12:45 | HSE and welfare walk | Assembly points, first aid, welfare actually functioning, statutory display | SITE_WALK 7
13:15 | Break
14:00 | Folder sampling — the RED and overdue list first | Go where the data already says the system is failing | FOLDER_SAMPLE
15:00 | Folder sampling — the rest, by area | Work down the sheet. Choose the sample yourself, never let it be selected for you | FOLDER_SAMPLE
16:30 | Draft findings and agree corrective actions | Agree owner and date with the project before you leave. Findings agreed later are resisted | FINDINGS
17:15 | Closing meeting — verbal score and critical findings | No surprises in the written report | DASHBOARD
AFTER THE AUDIT
When | Do this | Why | Done | Notes
Within 3 working days | Issue the written report with the score and all findings | A report issued a fortnight later is a historical document
At the target date | Verify closure physically, not on an email | A finding closed on assurance will recur at the next audit
Same month | Log the findings in 10.18 audit programme | Feeds the internal audit programme required by ISO 9001 cl.9.2
Next review | Present results at the management review | Required input under cl.9.3.2. Audits that never reach management review change nothing
RULES FOR THE AUDITOR
• | You must be independent of the project you are auditing. A Document Controller never audits their own site.
• | Choose the sample yourself. Never accept a sample selected by the auditee.
• | Test by inspection, not by asking. 'Do you do this?' is not an audit question.
• | Absence of evidence scores zero. It is not a maybe.
• | Photograph every finding. A finding without evidence will be argued.
• | Score honestly. A generous score helps nobody the day a claim arrives.

## DC_INTERVIEW
DOCUMENT CONTROLLER INTERVIEW
Ask these before sampling. The answers tell you where to look. Ask for evidence on every answer — 'we always do that' is not evidence. Record what they actually said.
Interviewee: ______________ Role: ______________ Date: __________ Interviewer: ____________
# | Question | Answer given | Evidence shown | Follow up
Set-up and authority
1 | Who nominated you as Document Controller, and can you show me that in writing?
2 | When was the numbering protocol issued to the contractors, and can you show me the transmittal?
3 | Who else can edit the registers?
4 | What do you do when a document arrives with a non-compliant number?
Daily working
5 | Walk me through what happens between a drawing arriving and it reaching the workface.
6 | How long does registration usually take? Show me the last five entries and their receipt dates.
7 | When did you last return a submission for a bad number?
8 | How do you know a reviewer has not overrun the SLA?
Revision control
9 | Show me the last revision that superseded a drawing. Where is the old one now?
10 | How do you get prints back from the workface, and what happens if one is missing?
11 | When did you last audit the drawing boards?
Under pressure
12 | In the busiest week of this project, what slipped?
13 | Has anyone ever asked you to backdate or amend a record? What did you do?
14 | Has a pour ever gone ahead without written permission? What happened?
KPI and reporting
15 | Show me the last KPI refresh timestamp.
16 | Which subjects were red last month, and what was done about them?
17 | Which register is closest to its capacity?
Support and resource
18 | Do you have enough time to do this properly? If not, what gets dropped first?
19 | What would you change about the system if you could?
20 | What do people most often get wrong when filing?

## SITE_WALK
SITE WALK INSPECTION SHEET
Physical inspection. Roughly half the critical findings on any document audit are found here, not in a folder. Do this before you sit down with the registers.
Project: ______________ Date: __________ Areas walked: ______________________ Accompanied by: ____________
# | What to look at | Location checked | Observed | Score | Photo ref. | Finding ref.
1. SITE OFFICE — DRAWING CONTROL
1 | Every drawing on the board carries an A-code suitability
2 | No superseded revision anywhere in the site office
3 | Drawing register on display matches what is on the board
4 | Superseded prints held for withdrawal are stamped and segregated
5 | No uncontrolled photocopies or marked-up prints in use
2. WORKFACE — DRAWINGS AND METHOD
6 | Prints held by foremen are current revision
7 | Approved method statement available at the activity
8 | Workforce can describe the method they were briefed on
9 | Approved mock-up or benchmark accessible for the finishing trade
10 | No work proceeding on a drawing marked for review or information
3. WORKFACE — PERMITS AND SAFETY
11 | Live permits displayed at the activity, not held in the office
12 | Permit precautions actually in place as described on the permit
13 | Permit within its stated validity period and location
14 | Gas test and isolation records attached where applicable
15 | Today's toolbox talk topic matches today's actual work
16 | Everyone at the workface has a valid induction and gate pass
4. QUALITY AT THE WORKFACE
17 | Pour card signed before the pour, with permission time recorded
18 | Cover blocks, spacers and reinforcement match the checklist entry
19 | Concealed work photographed before covering
20 | Test cubes marked and stored correctly
21 | Open NCR areas are physically quarantined or marked
22 | Calibration stickers current on instruments in use
5. INDUSTRIAL WORKFACE
23 | Welder ID on the weld matches the weld log and a current WPQ
24 | NDT markings present at the specified frequency
25 | Hydrotested lines tagged and reinstatement recorded
26 | Equipment alignment records available at the machine
27 | Temporary works carry a valid permit to load
28 | Coating DFT gauge readings available for the area inspected
6. STORES AND MATERIAL
29 | Material received matches the approved submittal brand and grade
30 | GRN raised for everything on the rack
31 | Test certificates held for material issued to the works
32 | Unapproved or rejected material segregated and marked
33 | Client-supplied material custody records available
34 | Storage conditions suit the material — cement, consumables, coatings
7. HSE AND WELFARE
35 | Emergency assembly points signed and visible in the site languages
36 | First aid and firefighting provision in place and in date
37 | Welfare facilities present and functioning, not provided for the day
38 | Statutory display board complete and current
39 | Waste segregated and disposal receipts available
8. DOCUMENT CONTROL PHYSICAL
40 | Registers being maintained daily, not in weekly bursts
41 | Filing matches the approved folder structure
42 | No project documents held only on personal laptops or phones
43 | Backup to the cloud DMS is current
44 | Access revoked for demobilised parties

## FOLDER_SAMPLE
FOLDER-BY-FOLDER SAMPLING SHEET
55 folders held at site or mirrored. Work down the list with the Document Controller. Score 2 fully met, 1 partly, 0 not met, N/A not applicable.
Project: ______________ Audit ref: __________ Date: __________ Auditor: ______________
# | Area | Folder | Cust. | Subject | Sample to take | What must be true | Records in LOG | Sampled | Defects found | Score | Finding ref.
01_CONTEXT_AND_GOVERNANCE
1 | 01 | 01.02_Stakeholders_and_Communication | BOTH | Stakeholder Register and Communication Plan | Stakeholder register | Statutory and neighbouring stakeholders identified · each has a named owner and frequency · none overdue for engagement
02_PLANNING
2 | 02 | 02.02_Project_Programme_Schedule_Control | BOTH | Project Programme and Schedule Control | Current programme | Logic-linked with no open ends · resource assumptions verified · baseline frozen with recorded approval · re-baselines justified
3 | 02 | 02.03_Milestone_Register_Payment_Linkage | BOTH | Milestone Register and Payment Linkage | Milestone register | Each milestone defined by verifiable criteria · payment certified only on demonstrated achievement · LD position assessed on every miss
4 | 02 | 02.04_LookAhead_Planning_Constraint_Management | BOTH | Look-Ahead Planning and Constraint Management | Last 4 look-aheads | Submitted weekly and derived from the approved programme · every constraint has a named owner and a date · PPC measured and trended
03_SUPPORT_AND_RESOURCES
5 | 03 | 03.01_Competence_and_Training | SITE | Induction, Training and Competency | 10 names from today's gate register | Induction recorded before first entry · competence certificates current for high-risk tasks · validity tracked with refresher before expiry
6 | 03 | 03.02_Resources_and_Productivity | SITE | Resource Deployment and Productivity | Last 4 weeks of returns | Deployment verified by physical count · compared against the histogram weekly · shortfall notified in writing when it occurred
7 | 03 | 03.06_Correspondence_Control | BOTH | Correspondence Control | 15 inward letters | Registered day of receipt · contractual ones flagged with a reply deadline · none overdue · reply reference recorded
8 | 03 | 03.07_Transmittal_Control | BOTH | Transmittal Control | 10 transmittals out | Numbered sequentially without gaps · purpose of issue stated · acknowledgement obtained or chased within 2 days · supersession recorded
9 | 03 | 03.08_Meetings_Minutes_Action_Tracking | BOTH | Meetings, Minutes and Action Tracking | 5 MOMs | Issued within 2 working days · actions numbered · single named owner each · open actions carried forward
10 | 03 | 03.09_Monitoring_and_Measuring_Equipment | SITE | Instrument Calibration Control | All instruments in use | Every acceptance instrument registered · calibration valid at the date of use · out-of-calibration triggers review of past measurements
04_DESIGN_AND_INFORMATION_MANAGEMENT
11 | 04 | 04.02_Drawings_and_Specifications | BOTH | Drawing Control and Issue | 15 drawings from the live GFC folder | Suitability is an A-code · registered within 24 hrs of receipt · transmittal exists for issue · superseded revision archived same day · withdrawal receipt on file
12 | 04 | 04.02_Drawings_and_Specifications | BOTH | Specifications and Technical Datasheets | 5 sections | Requirements measurable or testable · cited standards current · reconciled against BOQ
13 | 04 | 04.08_Shop_Drawings_and_Material_Submittals | BOTH | Material and Vendor Approval | 10 submittals | Reviewed within 7 days · checked against every specified parameter · sample retained at site · deviations formally accepted
14 | 04 | 04.08_Shop_Drawings_and_Material_Submittals | BOTH | Shop Drawing Review and Approval | 10 submissions | Reviewed within 7 working days · single clear status returned · no fabrication started before approval · resubmission count tracked
05_PROCUREMENT_AND_CONTRACTS
15 | 05 | 05.10_Customer_Supplied_Property | BOTH | Client Direct Purchase and FFE | 5 client-supplied items | Supply dates in the contract · inspected on delivery · custody transferred in writing · quantities reconciled
06_STATUTORY_AND_LAND
16 | 06 | 06.02_Statutory_Approvals_and_Permits | BOTH | Statutory Approvals and Permits | All approvals | All identified at inception and on the programme · queries answered within the authority's limit · nothing expiring within 60 days unactioned · conditions verified in the works
17 | 06 | 06.03_Labour_and_Statutory_Compliance | SITE | Labour Welfare and Statutory Compliance | All contractors on site | Registrations valid and re-checked not just verified once · PF and ESIC verified as remitted not merely deducted · welfare facilities physically inspected
18 | 06 | 06.04_Industrial_Statutory_Approvals | BOTH | Industrial Statutory Approvals and Licences | All industrial approvals | Factory plan approval BEFORE construction started · electrical inspectorate approval BEFORE energisation · conditions assigned and verified · full set before trial production
07_EXECUTION_AND_DELIVERY
19 | 07 | 07.01_Mobilisation_and_Site_Logistics | SITE | Site Logistics and Traffic Management | Current logistics plan | Planned by phase · lifting capacity verified against the heaviest lift · oversail consent in writing before erection
20 | 07 | 07.01_Mobilisation_and_Site_Logistics | SITE | Site Mobilisation and Establishment | Mobilisation records | Conditions precedent satisfied before entry · site layout approved before establishment · handover date formally recorded
21 | 07 | 07.02_Daily_Site_Records | SITE | Daily Progress Report | 20 days across the period, including the busiest week | Submitted by 10:00 next morning · labour verified by PMC not transcribed · quantities tied to WBS or BOQ · stoppages recorded with times · both signatures · no gaps in the date sequence
22 | 07 | 07.02_Daily_Site_Records | SITE | Progress Photography and Visual Record | Photo archive | Fixed vantage points at a set frequency · every image dated, located and labelled · all concealed work photographed before covering · backed up off-site
23 | 07 | 07.03_Site_Instructions_Client_Instructions | SITE | Site Instructions and Client Instructions | 10 instructions | Numbered · contract clause cited · cost and time impact recorded or expressly reserved · acknowledged · linked to a VO or CCR
24 | 07 | 07.04_Interface_Management_Between_Packages | SITE | Interface Management Between Packages | 5 interfaces | Identified at procurement not at site · single named owner · agreement converted to a drawing or schedule · verified physically before concealment
25 | 07 | 07.05_Work_Front_Release_Between_Trades | SITE | Work Front Release Between Trades | 5 front releases | Readiness criteria defined in advance · joint inspection with both trades · signed acceptance with snags listed · late release recorded against the handing trade
26 | 07 | 07.06_Method_Statements_and_Temporary_Works | SITE | Method Statement Review and Approval | 10 method statements | Reviewed within 5 working days · consistent with the JSA and ITP · briefed to the workforce before work started · re-approved on any method change
27 | 07 | 07.06_Method_Statements_and_Temporary_Works | SITE | Temporary Works Design and Control | 5 temporary works | Design independently checked to its category · permit to load issued after inspection · dismantling authorised in writing after strength verified
28 | 07 | 07.07_Material_Receipt_and_Traceability | SITE | Material Receipt, Inspection and Inventory | 10 GRNs | Checked against the approved submittal before acceptance · shortfall or damage noted on the challan at receipt · test certificate collected at receipt not at bill stage
29 | 07 | 07.08_Progress_Measurement_SCurve | BOTH | Progress Measurement and S-Curve | Last 3 measurement rounds | Measured physically against defined weightages · consistent rules of credit · same cut-off date each period · reconciled against certified value
30 | 07 | 07.09_Delay_Analysis | BOTH | Delay Analysis | All recorded delay events | Recorded contemporaneously with cause and times · criticality tested against the then-current programme · concurrency assessed
31 | 07 | 07.10_Recovery_Acceleration_Planning | BOTH | Recovery and Acceleration Planning | Any recovery plans | Responsibility established before cost agreed · measures specific and physically tested · tracked weekly against the plan
32 | 07 | 07.11_PEB_Structural_Steel_and_Surface_Protection | SITE | PEB and Structural Steel Fabrication and Erection | 5 fabrication lots | Fabrication drawings approved before cutting · dimensional inspection at works · coating DFT verified before dispatch · bolt torque recorded · frame surveyed before cladding
33 | 07 | 07.11_PEB_Structural_Steel_and_Surface_Protection | SITE | Surface Preparation, Painting and Insulation | 5 areas | Preparation verified against a comparator · ambient, substrate temp, RH and dew point recorded before every coat · individual DFT readings recorded not an average alone
34 | 07 | 07.12_Mechanical_Erection_Piping_and_Equipment | SITE | Equipment Erection, Alignment and Grouting | 5 equipment items | Foundation formally released · measured level and alignment values recorded not pass marks · re-checked after grouting and after piping · vendor written confirmation before first run
35 | 07 | 07.12_Mechanical_Erection_Piping_and_Equipment | SITE | Piping Fabrication, Erection and Hydrotest | 5 test packs | Test pack complete before pressurisation · supports installed before testing · full hold period achieved · gauge calibration valid · joints broken for test recorded as reinstated
08_QUALITY_HSE_AND_ENVIRONMENT
36 | 08 | 08.01_Quality_Plans_and_Inspection_Test_Plans | BOTH | Inspection and Test Plans | 5 ITPs | Approved before the activity started · every point has a criterion, a standard and a record · hold points marked as such
37 | 08 | 08.02_Inspection_Checklists_Pour_Cards | SITE | Inspection Checklists and Pour Cards | 10 pour cards | Inspected against ITP and drawing · measured values recorded not ticks · written permission before the pour · cover values recorded · photos linked
38 | 08 | 08.03_Testing_Test_Report_Control | SITE | Testing and Test Report Control | 15 test reports | Traceable to a specific element and location · sampling witnessed · specified vs achieved recorded · failures raised as NCRs · frequency per specification
39 | 08 | 08.04_Third_Party_Inspection | SITE | Third Party Inspection | 3 TPI reports | Agency accredited and independent of the contractor · findings closed with re-inspection · certificate filed against the element
40 | 08 | 08.05_MockUps_Benchmark_Approvals | SITE | Mock-Ups and Benchmark Approvals | 3 mock-ups | Built with actual materials, workforce and method · approved with client present · photographed · retained on site as benchmark
41 | 08 | 08.06_Control_of_Nonconforming_Output | SITE | Non-Conformance Reporting | 10 NCRs | Clause or specification cited · root cause beyond individual behaviour · corrective AND preventive action · closed against objective evidence
42 | 08 | 08.07_Hazard_Identification_Risk_Assessment | SITE | Hazard Identification and Risk Assessment | 5 assessments | Assessed before the activity started with the workforce involved · hierarchy of control applied not PPE alone · briefed in a language the workforce understands
43 | 08 | 08.08_Permit_Work | SITE | Permit to Work | 3 live permits at the workface | Precautions verified physically before issue · limited to a defined location and period · gas test and isolation recorded where applicable · closed formally with the area confirmed safe
44 | 08 | 08.09_Toolbox_Talks | SITE | Toolbox Talks | 5 attendance sheets | Held at the workface before the shift · topic drawn from today's actual work · attendance signed individually not in bulk by a supervisor
45 | 08 | 08.10_Incidents_and_Emergency_Preparedness | SITE | Emergency Preparedness and Drills | Last 2 drills | Held at planned frequency · evacuation timed and headcount reconciled · observations converted into closed actions
46 | 08 | 08.10_Incidents_and_Emergency_Preparedness | SITE | Incident and Near Miss Reporting | Last 5 incidents and near misses | All reported including near misses · scene preserved · statutory notification within the period · root cause reaches system failure not 'worker error'
47 | 08 | 08.11_Environmental_and_Sustainability | SITE | Environmental Monitoring and Waste Control | Last 3 monitoring rounds | Monitored at boundary and nearest receptor · exceedances recorded and mitigated with confirming re-monitoring · waste disposal receipts from authorised handlers
48 | 08 | 08.11_Environmental_and_Sustainability | SITE | Green Building and Sustainability Documentation | Credit evidence | Credits mapped to evidence and owner · evidence built as work proceeds not retrospectively · margin held above the threshold
49 | 08 | 08.12_Welding_and_NDT_Control | SITE | Welding and NDT Control | 10 welds | WPS supported by a PQR · welder qualified for the actual position, process and thickness · qualification current · NDT at specified extent · rejects triggered increased coverage
09_COMMERCIAL_AND_CHANGE
50 | 09 | 09.01_Interim_Bill_Verification_Certification | BOTH | Interim Bill Verification and Certification | Last 3 certificates | Certified within 10 days of a complete submission · quantities from joint measurement not the contractor's abstract · no certification against open NCRs · deductions carry a stated reason
51 | 09 | 09.02_Joint_Measurement | BOTH | Joint Measurement | 10 measurement sheets | Measured before concealment · signed by both parties at the time · location traceable · linked to a bill
52 | 09 | 09.03_Commitment_Expenditure_Register | BOTH | Commitment and Expenditure Register | Commitment register | Commitments recorded at award not at first invoice · compared to budget monthly · reconciled to client accounts
10_PERFORMANCE_HANDOVER_AND_IMPROVEMENT
53 | 10 | 10.01_Progress_Reporting_MIS | BOTH | Progress Reporting and MIS | Last 6 weekly reports | Constant cut-off and issue dates · progress verified by measurement · all six areas covered · issued on the due date
54 | 10 | 10.02_Project_KPIs_Performance_Measurement | BOTH | Project KPIs and Performance Measurement | KPI records | Every KPI has a formula, a source and a named measurer · baseline set at gate close · out-of-target KPIs carry a recorded cause
55 | 10 | 10.03_Presentations_Site_Visits_Reviews | BOTH | Presentations, Site Visits and Reviews | Last 3 reviews | Material circulated in advance and retained as delivered · decisions and client commitments minuted · actions tracked
56 | 10 | 10.04_Commissioning_and_Testing | SITE | Pre-Commissioning Checks | 5 checklists | Complete system list confirmed · checked against drawings and manufacturer requirements · punch items closed before energisation
57 | 10 | 10.04_Commissioning_and_Testing | SITE | Testing and Commissioning | 5 test records | Protocol and criteria agreed before testing · measured values recorded not pass ticks · integrated testing against a cause-and-effect matrix · full retest after modification
58 | 10 | 10.05_Snagging_and_Acceptance | SITE | Snagging and De-snagging | 2 zones | Snagging progressive not a single end exercise · every snag located and photographed · closure only after physical re-inspection
59 | 10 | 10.06_Handover_Dossier_Practical_Completion | BOTH | Handover Dossier and Practical Completion | Dossier index | Built continuously from project start · completeness tracked monthly · sections verified against the index
60 | 10 | 10.07_Operation_Maintenance_Manuals | BOTH | Operation and Maintenance Manuals | 3 manuals | Content and format specified in the contract · drafts before commissioning · reviewed by the FM team who will use them
61 | 10 | 10.08_Warranties_Guarantees | BOTH | Warranties and Guarantees | Warranty register | Collected through construction not at handover · start date, conditions and exclusions recorded · issued in the client's name
62 | 10 | 10.09_Mandatory_Spares_Consumables | BOTH | Mandatory Spares and Consumables | Spares schedule | Consolidated list from all contracts · verified against installed models · handed over against receipt before final payment
63 | 10 | 10.10_FM_Training_Soft_Landings | BOTH | FM Training and Soft Landings | Training records | Delivered on installed equipment before handover · attendance recorded and understanding verified · aftercare arrangement documented
64 | 10 | 10.11_Key_Access_Handover | BOTH | Key and Access Handover | Key schedule | Every construction key accounted for · locks re-keyed where unaccounted · handover against signed receipt
65 | 10 | 10.17_FAT_SAT_and_Performance_Test_Run | BOTH | Factory and Site Acceptance Testing | 5 test records | Protocol agreed at PO stage · every guaranteed parameter demonstrated with values · punch items categorised A or B · critical parameters repeated at SAT
66 | 10 | 10.17_FAT_SAT_and_Performance_Test_Run | BOTH | Performance Guarantee Test Run and Trial Production | Test run records | Parameters, duration and method fixed in the contract · prerequisites verified before start · full duration without interruption · logs signed during the run

## FINDINGS
SITE AUDIT FINDINGS AND CORRECTIVE ACTION
One finding for every score below 2, from either the folder sampling or the site walk.
# | Finding ref. | Source | Ref. no. | Folder / location | Finding — what was actually found | Photo ref. | Severity | Root cause | Corrective action | Preventive action | Owner | Target date | Closed on | Days open | Overdue? | Verified by | Status
1 | SF-001 | Site walk | W-07 | L3 workface, grid D4 | Two prints of DR-ST-0142 rev C01 in use by the shuttering foreman. C02 issued 11 days earlier | IMG-0412 | Critical | Withdrawal not enforced when C02 issued; no receipt taken | All C01 prints recovered against receipt same day; boards audited | Withdrawal receipt made a precondition of issuing the next revision | Document Controller | 2027-08-15 |  |  |  |  | Open
Formulas:
Days open = IFERROR(IF([Target date]="","",IF([Closed on]="",TODAY()-[Target date],[Closed on]-[Target date])),"")
Overdue? = IFERROR(IF(OR([Target date]="",[Status]="Closed"),"",IF(TODAY()>[Target date],"Yes","No")),"")