## Dashboard
Quality Performance Report - Project # - Week 13
This week Concreting |  | No. of sample last week |  | Sample Pass in 7 days strength | Sample fail in 7 days strength |  | Sample fail in 28 days strength |  | Total NCR Open
3200 m3 |  | 120 |  | 110 | Total 10 samples has not been pass in 7 days strength, PMC team check those at 28 days strength if not pass then raise NC |  | 0 |  | 0
Quality Performance - Overalll | [7 empty] | Bad Quality Practice - Week 13
Site Observation Success Rate | 86.67%
Site Instruction Success Rate | 93.33%
Non Conformity Success Rate | 100%
Previous Week Quality Score
QPI Week 12 | 88%
QPI Week 11 | 85%
QPI Week 10 | 80%
Quality at a Glance Week #13 |  |  | Checklist Summary |  |  | Compressive Test Result
QPI
Concrete
Reinforcement
NCR
QA Office
A Quality Control office of 3 x 2.5 m2 working good. No Action Req.
A Quality Assurance Plan for all materials is aligned with contract req.
QA Plan
Tests
Compressive Strength Tests and Slump Tests are performed every certain period as required
Tests’ Registers
Registers for every test are maintained properly by the quality personnels
Cleaning
Weekly cleaning of the cube pond is performed by the personnels.
QPI
Quality Perfromance Rate
400 mm
93.33%

## Sheet2
Row Labels | Sum of No of Checklist Filled
Civil | 10
Electrical | 3
ELV | 6
Fire | 3
Handover | 0
Interior | 3
Mechanical | 3
Mobilization | 1
PC | 5
PD | 5
PEB | 5
Plumbing | 3
Safety | 5
Workpermits | 0
Grand Total | 52

## Sheet1
Sr No | File Name | Work Category
1 | Checklist For Pre-Construction & Mobilization - Civil | Mobilization
2 | Checklist For Pre-Construction & Mobilization - Electrical | Mobilization
3 | Checklist For Pre-Construction & Mobilization - Interiors | Mobilization
4 | Checklist For Pre-Construction & Mobilization - Mechanical | Mobilization | Work Category | No of Checklist Filled
5 | Checklist For Pre-Construction & Mobilization - PEB | Mobilization | Mobilization | 1
6 | Checklist For Pre-Construction & Mobilization - Plumbing | Mobilization | Civil | 10
7 | Checklist For Pre-Construction & Mobilization -Fire | Mobilization | PD | 5
8 | Aggregate Crushing Value Test- Nominal Size | Civil | PC | 5
9 | Aggregate Impact Value Test | Civil | PEB | 5
10 | Aggregate Specific Gravity & Water Absorption | Civil | Mechanical | 3
11 | Anti Termite Report | Civil | Electrical | 3
12 | Checklist For Anchor Bolt Fixing û Peb | Civil | Plumbing | 3
13 | Checklist For Block Work | Civil | Fire | 3
14 | Checklist For Brick Masonry Work | Civil | Interior | 3
15 | Checklist For Chamber Fixing | Civil | ELV | 6
16 | Checklist For Demolition Work | Civil | Safety | 5
17 | Checklist For Excavation Work | Civil | Workpermits | 0
18 | Checklist For Filling Work | Civil | Handover | 0
19 | Checklist For Floor Trimix Work | Civil
20 | Checklist For Floor Trimix û Densification Work | Civil
21 | Checklist For Gp2 Filling | Civil
22 | Checklist For Handing Over Work | Civil
23 | Checklist For Lean Trimix (Groove Work) | Civil
24 | Checklist For Metal Soiling Work | Civil
25 | Checklist For P.C.C Work | Civil
26 | Checklist For Paver Block Work | Civil
27 | Checklist For Plastering Work | Civil
28 | Checklist For Pre-Cast Cover Slabs | Civil
29 | Checklist For R.C.C Pipe Work | Civil
30 | Checklist For Road Trimix Work | Civil
31 | Checklist For Shuttering | Civil
32 | Checklist For WBM.GSB.WMM | Civil
33 | Concrete Cube Testing Form | Civil
34 | Concrete Pre-Pour & Post Pore Inspection Report | Civil
35 | Determination Of Fineness Of Cement | Civil
36 | Field Dry Density By Core Cutter | Civil
37 | Field Dry Density By Sand Replacement | Civil
38 | Flakiness & Elongation Index | Civil
39 | Incoming Material Inspection Report | Civil
40 | Joint Measurement Record | Civil
41 | Pour Card | Civil
42 | RMC Plant Calibration Report (Admixture) | Civil
43 | RMC Plant Calibration Report (Cement) | Civil
44 | RMC Plant Calibration Report (CoarseFine Aggregate) | Civil
45 | RMC Plant Calibration Report (Water) | Civil
46 | Reinforcement Cage Inspection Report | Civil
47 | Sieve Analysis Of Coarse Aggregate (10MM) | Civil
48 | Sieve Analysis Of Coarse Aggregate (20MM) | Civil
49 | Sieve Analysis Of Coarse Aggregate (GSB) | Civil
50 | Sieve Analysis- Fine Aggregate (Sand) | Civil
51 | Sieve Analysis- Masonry Mortor | Civil
52 | Silt Content In Sand | Civil
53 | Survey Check Report | Civil
54 | Water Proofing Report | Civil
55 | PD Backfilling Around Drain | PD
56 | PD Drain Cover Grating Fixing | PD
57 | PD Excavation For Drain Alignment | PD
58 | PD Final Certification | PD
59 | PD Handling & Placement Of Pre-Cast Drain Units | PD
60 | PD Joint Treatment & Sealing | PD
61 | PD Pre-Cast Drain Material Inspection | PD
62 | PD Testing & Final Inspection | PD
63 | PC Checklist For Backfilling & Finishing Around Wall | PC
64 | PC Foundation & Excavation For Posts | PC
65 | PC Handling & Placement Of Panels | PC
66 | PC Handling, Lifting & Placement Of Posts | PC
67 | PC Joint Treatment & Sealing | PC
68 | PC Pre-Cast Panel & Post Material Inspection | PC
69 | PC Testing & Final Inspection | PC
70 | EOT Crane Work Checklist - Electrical installation | PEB
71 | EOT Crane Work Checklist - Handover & documentation | PEB
72 | EOT Crane Work Checklist - Mechanical installation | PEB
73 | EOT Crane Work Checklist - PEB Structure preparation | PEB
74 | EOT Crane Work Checklist - PRE-Construction-Civil readiness | PEB
75 | EOT Crane Work Checklist - Rail installation | PEB
76 | EOT Crane Work Checklist - Testing & commissioning | PEB
77 | PEB Alignment Checking Checklist | PEB
78 | PEB Final Alignment Checking Checklist | PEB
79 | PEB Finished Material Inspection Checklist (Before Dispatch û Plant Level) | PEB
80 | PEB Handover Checklist | PEB
81 | PEB Raw Material Inspection Checklist | PEB
82 | PEB Roof Sheeting & Cladding Material Inspection Checklist | PEB
83 | Checklist For ( MVRV,VRF ) System | Mechanical
84 | Checklist For AHU Installation | Mechanical
85 | Checklist For Air Compressor | Mechanical
86 | Checklist For Chiller | Mechanical
87 | Checklist For Cooling Tower | Mechanical
88 | Checklist For Ducting | Mechanical
89 | Checklist For Mechanical Piping | Mechanical
90 | Checklist For Testing & Commissioning | Mechanical
91 | Checklist For (VDB,DB,SDB,PDB) | Electrical
92 | Checklist For Cable Laying & Fixing | Electrical
93 | Checklist For Cable Trays & Raceways | Electrical
94 | Checklist For Dg Set & Amf Panel | Electrical
95 | Checklist For Earthing & Lightning Protection | Electrical
96 | Checklist For Final Testing & Commissioning | Electrical
97 | Checklist For Ht Lt Panels (PCC, MCC, APFC) | Electrical
98 | Checklist For Lighting & Power Points | Electrical
99 | Checklist For Motors, Vfds & Bus Ducts | Electrical
100 | Checklist For Solar Pv System | Electrical
101 | Checklist For Transformer | Electrical
102 | Checklist For Ups & Battery Bank | Electrical
103 | Checklist For Drainage System | Plumbing
104 | Checklist For Plumbing Fixtures & Accessories | Plumbing
105 | Checklist For Rainwater Harvesting Stormwater System | Plumbing
106 | Checklist For Sewage & Stp System | Plumbing
107 | Checklist For Testing & Commissioning | Plumbing
108 | Checklist For Water Supply System | Plumbing
109 | Checklist For Final Testing & Commissioning | Fire
110 | Checklist For Fire Alarm & Detection System | Fire
111 | Checklist For Fire Pump Room | Fire
112 | Checklist For Hydrant System | Fire
113 | Checklist For Sprinkler System | Fire
114 | Checklist For Acoustic & Soundproofing Works | Interior
115 | Checklist For Dado Flooring | Interior
116 | Checklist For Doors | Interior
117 | Checklist For False Ceiling Works | Interior
118 | Checklist For Faτade External Works | Interior
119 | Checklist For Final Testing, Snagging & Handover | Interior
120 | Checklist For Flooring Works | Interior
121 | Checklist For Health, Safety & Accessibility Compliance | Interior
122 | Checklist For Joinery, Carpentry & Modular Furniture | Interior
123 | Checklist For Landscaping & Exterior Hardscape | Interior
124 | Checklist For Loose Furniture & Soft Furnishings | Interior
125 | Checklist For Mep Coordination In Interiors | Interior
126 | Checklist For Partition Works | Interior
127 | Checklist For Sanitary Fittings & Washroom Interiors | Interior
128 | Checklist For Signage & Wayfinding | Interior
129 | Checklist For Staircase, Railing & Balustrade | Interior
130 | Checklist For Wall Finishes | Interior
131 | Checklist For Windows & Glazing | Interior
132 | Natural Stone Fixing û Site Execution One-Liner Checklist | Interior
133 | Checklist For Access Control & Attendance System | ELV
134 | Checklist For Building Management System (Bms) | ELV
135 | Checklist For Cctv Surveillance System | ELV
136 | Checklist For Data & Networking (Structured Cabling) | ELV
137 | Checklist For Fire Alarm & Detection System (Elv Scope) | ELV
138 | Checklist For Public Address & Bgm System | ELV
139 | Checklist For Specialized Systems (If Applicable) | ELV
140 | Checklist For Telephone & Intercom System | ELV
141 | Checklist For Testing & Commissioning û Combined Checks | ELV
142 | Accident Report | Safety
143 | Man Hour Log | Safety
144 | Monthly HSSE Report | Safety
145 | NCR | Safety
146 | Near Miss | Safety
147 | Observation - Unsafe Act | Safety
148 | Safety Orientation-training | Safety
149 | Safety Summary | Safety
150 | Site Instruction | Safety
151 | Tool Box Talk | Safety
152 | Unsafe Act Summary | Safety
153 | Confined Space Entry Work Permit | Workpermits
154 | General Permit to Work (PTW) | Workpermits
155 | Hot Work Permit | Workpermits
156 | Permit for Excavation | Workpermits
157 | Permit for Lifting Operation(s) | Workpermits
158 | Permit for Night Work | Workpermits
159 | Permit for Work at Height | Workpermits
160 | Permit to (Erect,Alter,Dismantle Scaffold) | Workpermits
161 | Permit to Work û Risers & Lift Shafts | Workpermits
162 | Checklist For Civil Handover | Handover
163 | Checklist For Electrical Handover | Handover
164 | Checklist For Fire Handover | Handover
165 | Checklist For Interior Handover | Handover
166 | Checklist For Mechanical Handover | Handover
167 | Checklist For PEB Handover | Handover
168 | Checklist For Plumbing Handover | Handover

## SOR Log
Sr.no. | Observation | Total | Open | Close | Closure Rate | Sr. No. | Name of Equipment | Unit | Total Number
1 | Site Observation | 75 | 10 | 65 | 86.67% | 1 | Compression Testing Machine | No | 1
2 | Site Instruction | 75 | 5 | 70 | 93.33% | 2 | Slump Cone Test Apparatus | Set | 1
3 | NCR | 1 | 0 | 1 | 100% | 3 | Steel Moulds | No | 25
|  |  |  | Average | 93.33% | 4 | Digital Moisture Meter | No | 1
[6 empty] | 5 | Weighing Balance | No | 1
[6 empty] | 6 | Thermometer | No | 1
Sr.no. | Observation | Open | Close
1 | Site Observation | 10 | 65
Sr.no. | Observation | Open | Close
2 | Site Instruction | 5 | 70
Sr.no. | Observation | Open | Close
3 | NCR | 0 | 1

## Cube Test
Sample # | Compressive strength at 7 days | IS code lower limit
1 | 19.07 | 17
2 | 23 | 17
3 | 22.24 | 17
4 | 18.03 | 17
5 | 18.24 | 17
6 | 19.16 | 17

## CAR register
NON CONFORMANCE AND CORRECTIVE ACTION REQUEST (CAR ) REGISTER
No. | NCR / CAR Issue Date | Type | Contractor | Brief Description of Non Conformance | Location | Planned Closure Date | Actual Closure Date | Status
1 | 2024-05-10 | Quality | RIAD | According to the drawing of the UG Tank (Job: 35/2023, Drawing No: 1, Date: 05-02-2024), note point 8 specifies the requirement for a water stopper to be installed at the construction joint of the water tank. The water stopper should be 150 mm wide and 5 mm thick, made of PVC material. However, despite this specification, the contractor, project manager, and client have disagreed on the provision of this water stopper. If the water stopper is not installed at the joint as per the drawing, there is a risk of water leakage occurring at the joint. Therefore, it's essential to adhere to the specified requirements to prevent potential water leakages and ensure the integrity of the construction. | India | 2024-05-12 |  | Open
Health and Safety
Environmental
| Quality |  |  |  | Australia
China
Hong Kong
India
Indonesia
Japan
Korea
Philippines
Singapore
Taiwan
Thailand
Vietnam

## Quality Assurance Plan - Detail
Client LOGO |  | Quality Assurance Plan
Project |  | Safari Industrial Plant Halol |  |  | LEGENDS
Client |  | Safari India Pvt. Ltd. |  |  | BBS - Bar Bending Schedule |  | MTC - Material Test Certificate |  | RCC - Reinforced Cement Concrete
Design Consultant |  | HCP Design Consultant |  |  | CUM - Cubic Meter |  | PCC - Plain Cement Concrete |  | SQM - Square Meter
PM Consultant |  | Sharnam Project Managemnet Consultants |  |  | HSE - Health Safety & Environment |  | QA - Quality Assurance |  | TBM - Temporary Bench Mark
Contractor |  | Shapoorji Pallonji Construction Pvt. Ltd. |  |  | IS - Indian Standard |  | QC - Quality Control |  | TPC - Third Party Confirmation
Sr.No. | Activity | Description of Activity / Material | Frequency of check | Code of Conformance | Test agency | Contractor |  | PMC | CLIENT | Records and documents to be Maintained | Remarks if any
[6 empty] | Performer | Checker | Checker | Checker
1 | Site Survey | Confirmation of Calibrated Equipment | Service agency due date |  | Approved external agency |  | QC Engr | Review | Random | Calibration Certificate | Pending
|  | Building lay out and setback | Every layout | Approved Drawing |  | Surveyor | Site Engr | Witness | Witness | Setting out plan | Completed
|  | Bench Mark shifting & TBM Preparation | Once established | Client reference |  | Surveyor | Site engr | Witness | Witness | Level book | Completed
2 | Excavation | Required Safety norms coordinate to HSEM Process. | Every foundation and trench |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Pending
|  | Disposal of black cotton soil and yellow soil in suggested area | Every foundation and trench | Client reference |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation for completion of survey activities. | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of Layout, alignment and size of excavation | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Pending
|  | Confirmation of underground utilities | Every foundation and trench | Client reference |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of drawing and drawing revision | Every foundation and trench | Updated Drawing Register |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation for joint inspection reports | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Pending
3 | Plain Cement Concrete | Confirmation of location, excavated pit bed, levels, free from slush and well compacted. | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of Layout, alignment and size of excavation | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of formwork | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of drawing and drawing revision | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation for joint inspection reports | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of Concrete grade/Nominal Mix | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of required tools and tackles | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of concrete top surface | Every foundation and trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
4 | Reinforcement | Required Safety norms coordinate to HSEM Process. | Each structure & Element |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Pending
|  | Confirmation of rolling margin testing | Every consignment | IS-1786 | Site Laboratory | QC/QA Engr | QC/QA Engr | Witness | Random | Work Check List | Pending
|  | Chemical Analysis of reinforcement steel | Every lot | IS-432 | Manufacturer Test Certificate | QC/QA Engr | QC/QA Engr | Review | Random | MTC | Pending
|  | Physical test of reinforcement steel | Every lot | IS-1786 | Approved external lab | QC/QA Engr | QC/QA Engr | Review | Random | TPC | Pending
|  | Confirmation of BBS preparation and approval | Each structure & Element | Approved Drawing & IS 2502 |  | Site Engr | QC Engr | Review | Approve | Bar Bending Schedule | Pending
|  | Confirmation of reinforcement Numbers, Shape, Dia, cutting and bending. | Each structure & Element | Approved Drawing & BBS |  | Site Engr | QC Engr | Witness | Random | Work Check List | Pending
|  | Confirmation for reinforcement placing | Each structure & Element | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Pending
|  | Confirmation of clear concrete cover to reinforcement | Each structure & Element | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Pending
|  | Confirmation of provision for Chairs and spacers( Numbers, Shape, Length and position) | Each structure & Element | Approved Drawing & BBS |  | Site Engr | QC Engr | Witness | Random | Work Check List | Pending
|  | Confirmation of reinforcement lapping | Each structure & Element | Approved Drawing & IS 456 |  | Site Engr | QC Engr | Witness | Random | Work Check List | Pending
|  | Confirmation of reinforcement welding | As per requirement | Approved Drawing/ Client reference |  | Site Engr | QC Engr | Witness | Random | Work Check List | Pending
|  | Confirmation of Binding wire | Once in Every Source | IS 456 | Site Laboratory | QC/QA Engr | QC/QA Engr | Witness | Random | Test Report | Pending
5 | Formwork | Required Safety norms coordinate to HSEM Process. | Each structure & Element |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of level reference. | Each structure & Element | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for all the plates / plywood, cleaned and polished properly | Each structure & Element |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of shuttering oil/polish material |  | IS 456 |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for suitability, stability, safety, rigidity of assembled forms | Each structure & Element |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for alignment, verticality, right angle, and diagonals of shuttering faces | Each structure & Element | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of shuttering supports and bracings. | Each structure & Element |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of adequate of concrete cover blocks. | Each structure & Element |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of cutouts, sleeves and other embedded items to fix with formwork | Each structure & Element | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of shuttering gapes, joints, holes and tie rods | Each structure & Element | IS 456 & DESIGNER SPECIFICATION |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of deshuttering/form dismantling time duration | Each structure & Element |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
6 | Concreting | A) Material Confirmation
a. Cement
|  | ● Type of Material |  | Client Reference/ Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Grade of Material |  | Client Reference/ Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Fineness | Once in every lot | IS-4031 part-1, IS 269 | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | ● Setting time | Once in every lot | IS-4031 part-4 &5, IS 269 | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | ● Soundness | Once in every lot | IS-4031-part3, IS 269 | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | ● Compressive strength | Once in every lot | IS-4031-part6, IS 269 | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | ● Chemical Composition | Once in every lot | IS code for relevant grade | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
b. Coarse Aggregate
|  | ● Source of Material | Once Initial Start | Client Reference |  | Site Engr | QC Engr | Review | Approve
|  | ● Incoming material test before unloading ( over size/ finer ) | Every Consignment |  |  | Site Engr | QC Engr | Witness | Random | Register/Note | Pending
|  | ● Sieve analysis | Every 200 cum | IS-2386 Part-1, IS 383 | Site Lab/Approved external lab | Site Engr | QC Engr | Witness | Random | Test Report | Pending
|  | ● Impact value | Once in every source | IS-2386 Part-IV, IS 383 | Approved external lab | Site Engr | QC Engr | Witness | Random | TPC | Pending
|  | ● Crushing value | Once in every source | IS-2386 , IS 383 | Approved external lab | Site Engr | QC Engr | Witness | Random | TPC | Pending
|  | ● Flakiness & Elongation | Every 200 cum | IS-2386 , IS 383 | Site Lab/Approved external lab | Site Engr | QC Engr | Witness | Random | Test Report | Pending
|  | ● Specific gravity | Once in every source | IS-2386 , IS 383 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Pending
|  | ● Abrasion Value | Once in every source | IS-2386 , IS 383 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Pending
|  | ● Water Absorption | Once in every source | IS-2386 , IS 383 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Pending
c. Fine Aggregate
|  | ● Source of Material | Once Initial Start | Client Reference |  | Site Engr | QC Engr | Review | Approve | Test Report | Completed
|  | ● Incoming material test before unloading ( Silt content & deleterious material) | Every Consignment | IS-383 | Site Lab | QA/QC Engr | QA/QC Engr | Witness | Random | Test Report | Completed
|  | ● Sieve analysis | Every 200 cum | IS-383 | Site Lab | Site Engr | QC Engr | Witness | Random | Test Report | Completed
|  | ● Fineness | Every 200 cum | IS-383 | Site Lab | Site Engr | QC Engr | Witness | Random | Test Report | Completed
|  | ● Specific gravity | Once in every source | IS-2386 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Deleterious materials | Once in every source | IS-383 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Water Absorption | Once in every source | IS-383 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Loose Bulk Density | Once in every source | IS-383 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
d. Water
|  | ● pH Value | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Limits of Acidity | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Limits of Alkalinity | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Percentage of solid Organic & inorganic material | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Sulphate | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Chloride | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Suspended Solid | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Color Hazen Units | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Odour | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Hardness | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Fluoride | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
|  | ● Turbidity | Once in every source | IS 3025, IS 456 | Approved external lab | Site Engr | QC Engr | Review | Random | TPC | Completed
e. Admixture
|  | ● Material | Every Consignment | IS 9103 | Manufacturer | Site Engr | QC Engr | Review | Random | MTC | Pending
|  | B) Mix Design/Trial Mix | Once in initial | Client Reference | Site Lab |  |  |  |  | MTC | Completed
C) Concrete confirmation
|  | ● Slump Test | Every pour start | IS-516 | Site Lab | Site Engr | QC Engr | Witness | Random | Concrete log | Completed
|  | ● Concrete Compressive Strength check by cube Test |  | IS-456 | Site Lab | Site Engr | QC Engr | Witness | Random | Register/Note | Completed
|  | ● Actual Standard Deviation | Once in month |  | Site Lab | Site Engr | QC Engr | Witness | Random | Test Report | Completed
D) Pre-Inspection
|  | ● Confirmation of PCC level | Each structure & Element | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of Reinforcement check points | Each structure & Element | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of Formwork check points | Each structure & Element | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of embedded bolts/plates/pipe sleeves, etc. | Each structure & Element | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of material used for concrete | Each structure & Element | Concrete Batch Report |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● All required equipment arrangement |  |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Conformation of concreting time |  |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
D) Post-Inspection
|  | ● Confirmation of cube casting & testing | Each structure & Element | IS-456 |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of concrete surface, levels and surface finishing | Each structure & Element |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
7 | Back Filling | Required Safety norms coordinate to HSEM Process.
|  | Confirmation of existing ground level | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of finished ground level for all areas | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for satisfactory stripping of top soil | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for cutting of earth to required level | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of layer by layer filling | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of material quality | Each layer |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of soil MDD and OMC | Once in every source | Morth Specification | Approved external lab | QA/QC Engr | QA/QC Engr | Review | Random | TPC | Completed
|  | Check for sprinkling of water and adequate rolling ; kindly avoid ware sprinkling for lime-sand filling | Each layer |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for dressing of formed surface upto desired FGL | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of compaction by core cutter testing for soil filling | 1 test / 500 sqm | Morth Specification | Site Lab | QA/QC Engr | QA/QC Engr | Review | Random | Test Report | Completed
|  | Confirmation of compaction by sand replacement testing for lime-sand filling | 1 test / 500 sqm | Morth Specification | Site Lab | QA/QC Engr | QA/QC Engr | Review | Random | Test Report | Completed
8 | Granular Sub Base for raft, flooring, and road works | Required Safety norms coordinate to HSEM Process. |  |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of material source | Once Initial Start | Client Reference |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of location, level and area for GSB | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for cleaning of location | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of layer thickness of GSB | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of required rolling | Each layer |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Visual Confirmation of GSB compacted surface | Each layer |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | GSB Field Density confirmation by Sand replacement test | 1 test / 500 sqm | Morth Specification | Site Lab | QA/QC Engr | QA/QC Engr | Witness | Random | Test Report | Completed
|  | Gradation & Moisture Content confirmation for Grade 01 material | 1 test / 200 cum | Morth Specification | Site Lab | QA/QC Engr | QA/QC Engr | Witness | Random | Test Report | Completed
|  | Confirmation of Plasticity Index, Standard Proctor Test, CBR, 10% fine value of GSB | Once in every source | Morth Specification | Approved external lab | QA/QC Engr | QA/QC Engr | Review | Random | TPC | Completed
9 | Wet Mix Macadam for raft, flooring, and road works | Required Safety norms coordinate to HSEM Process. |  |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of material source | Once Initial Start | Client Reference |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of location, level and area for WMM | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for cleaning of location | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of layer thickness of WMM | Each layer | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of required rolling | Each layer |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Visual Confirmation of WMM compacted surface | Each layer |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | WMM Field Density confirmation by Sand replacement test | 1 test / 500 sqm | Morth Specification | Site Lab | QA/QC Engr | QA/QC Engr | Witness | Random | Test Report | Completed
|  | Gradation confirmation | 1 test / 100 cum | Morth Specification | Site Lab | QA/QC Engr | QA/QC Engr | Witness | Random | Test Report | Completed
|  | Flakiness and Elongation value confirmation | Once in every source | Morth Specification | Approved external lab | QA/QC Engr | QA/QC Engr | Review | Random | TPC | Completed
|  | Confirmation of Abrasion value, Aggregate Impact Value | Once in every source | Morth Specification | Approved external lab | QA/QC Engr | QA/QC Engr | Review | Random | TPC | Completed
10 | Anti Termite Treatment | Required Safety norms coordinate to HSEM Process. |  |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Material physical and chemical properties | Each lot | Manufacturer confirmation | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | Check for required tools and tackles | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for chemical and water proposal | Each structure | IS 6313 |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for hole marking and rate of spray under floor | Each structure | IS 6313 |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of area/location for treatment | Each structure | IS 6313 |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of sufficient chemical and water proposal applied | Each structure | IS 6313 |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
11 | Masonry Work - Brick/ Concrete Block | Required Safety norms coordinate to HSEM Process. |  |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | A) Prior to masonry | [8 empty] | Completed
|  | ● Check for area cleaning | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for material stacking on site location for use | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for material wet surface | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for door, window and other opening frame erection or installation completion | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of line and level marking for masonry | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of mortar proposal | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of masonry bond | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for bee holes and Weep holes | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | B) During masonry | [8 empty] | Completed
|  | ● Confirmation of dimensions | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of door, window and other opening size | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for margins left for plastering jambs | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for plumb, line and levels | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for racking of joints to receive plastering or pointing | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | C) After masonry | [8 empty] | Completed
|  | ● Check for curing arrangement | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for all mortar joints are raked and cleaned | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for thee filling of all bee holes | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for weep holes are clean and serviceable | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check that all flatwork has been cleaned and is scraped free of mortar splatters | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check all waste material has been piled in designated trash area | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List
D) Material Confirmation
|  | Cement | As per concreting item
|  | Fine Aggregate | As per concreting item
|  | Water | As per concreting item
|  | Confirmation of Density in oven dry condition, & Compressive Strength in Mpa for concrete block | 1 test / 5000 no's | IS 2185 | Approved external lab | QA/QC Engr | QA/QC Engr | Review | Random | TPC | Completed
|  | Confirmation of measurement, water absorption, compressive strength in Mpa, effloresces, shrinkage | 1 test / 50000 no's |  | Approved external lab | QA/QC Engr | QA/QC Engr | Review | Random | TPC | Completed
12 | Plastering | Preparatory arrangement of surface preparation like raking of joints, removal of loose mortar and fixing chicken mesh at RCC and Masonry joints ant wetting surface | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Proportion of cement mortar, mixing and placing in location | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Checking of alignment, thickness, verticality in line of construction drawing | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
13 | Flooring | Required Safety norms coordinate to HSEM Process.
A) Vacuum Dewatering Floor
|  | ● Check area for cleanliness before concreting | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for stability of formwork | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check alignment, level, joint sealing | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for reinforcement size, spacing, location, numbers, overlapping, welding, joint, hooks, bends, and cover | Each structure | Approved Drawing & Approved Bar Bending Schedule |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check process of concrete pouring and grade of concrete | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check quantity of concrete to be poured | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for workability of concrete at site before pouring | Each structure | Approved Trial Mix |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of equipment and machinery for work | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for concrete top level | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for vacuum dewatering as per the specification | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of finished floor surface | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of curing arrangement | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
A) Tile Flooring- Vitrified/Ceramic
|  | ● Check for the tile material approval | Each structure | Client Reference | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | Material Data Sheet | Completed
|  | ● Check for the surface cleaning-free from loose mortar, laitance etc. | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Tiles are sound, non-sbsorbingflat and true to shape with straight edge | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for fixing of level pads | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● All tiles which are used in work have soaked | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of mortar proposal | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Check for bedding of cement mortar properly levelled, temped, and corrected to desire level or thickness | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Bed mortar roughened before laying tile | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of tile laying pattern | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of tile joints | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of floor final level | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | ● Confirmation of epoxy grouting for tile joint filling | Each structure | Client Reference | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | Material Data Sheet | Completed
|  | ● Confirmation of curing arrangement | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
14 | Wall tile work-Dado fixing | Required Safety norms coordinate to HSEM Process. |  |  |  | Site Engr | QA/QC Engr | Witness | Random | Work Check List | Completed
|  | Check for the tile material approval | Each structure | Client Reference | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | Material Data Sheet | Completed
|  | Check for the surface cleaning-free from loose mortar, laitance etc. | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Tiles are sound, non-sbsorbingflat and true to shape with straight edge | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for fixing of level pads | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | All tiles which are used in work have soaked | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of mortar proposal | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for bedding of cement mortar properly levelled, temped, and corrected to desire level or thickness | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Bed mortar roughened before laying tile | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of tile laying pattern | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of tile joints | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of top final level | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of epoxy grouting for tile joint filling | Each structure | Client Reference | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | Material Data Sheet | Completed
|  | Confirmation of curing arrangement | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of Dimension, surface quality, physical properties, chemical properties | Each lot | IS 15622 | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
15 | RCC hume pipe laying | Required Safety norms coordinate to HSEM Process. | Each trench
|  | Confirmation of trench section | Each trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of trench gridline | Each trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of Sand/PCC top level | Each trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of Sand/PCC thickness | Each trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Conformation of pipe diameter | Each trench | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of pipe gradient | Each trench | Approved Drawing | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | Confirmation of pipe condition | Each trench |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of pipe collar thickness and dia | Each Joint | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of pipe and collar fixing mortar proposal | Each Joint | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of backfilling with proper compaction | As per backfilling item | [7 empty] | Completed
|  | Confirmation of three edge bearing load to produce 0.25mm crack KN/Linear meter | Each lot | IS 458 | Manufacturer / Approved external lab | QA/QC Engr | QA/QC Engr | Review | Random | MTC/TPC | Completed
|  | Confirmation of unlimited load KN/Linear meter | Each lot | IS 458 | Manufacturer / Approved external lab | QA/QC Engr | QA/QC Engr | Review | Random | MTC/TPC | Completed
16 | Grouting of Insert Plate and Anchor Bolts | Required Safety norms coordinate to HSEM Process. |  |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for pedestal top surface cleaning | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of formwork | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of grouting material | Each structure | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of grouting material mixing ratio | Each structure | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of finished grouted surface | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of compressive strength by cube testing | 1 set (6 cubes) / Day for each deferent structure for 7 days and 28 days testing | Manufacturer Technical Data Sheet | Site Lab | QA/QC Engr | QA/QC Engr | Review | Random | Test Report | Completed
17 | Painting | Required Safety norms coordinate to HSEM Process. |  |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | A) Application of white putty | [8 empty] | Completed
|  | Check for the surface cleaning from all masking tape, loos mortar, etc. | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of material | Each lot | Client Reference | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | Confirmation of material mixing according to manufacturer specification | Each structure | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of 1st coat application | Each structure | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of application and covered all joints like slab and beam, column and beam | Each structure | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | confirmation of glass paper application before start second coat | Each structure | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | confirmation of final finishing | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of tensile adhesion test @ 28 days | Each lot | EN 1348 | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | Confirmation of compression adhesion test @ 28 days | Each lot | EN 196 | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | Confirmation of initial and final setting setting time | Each lot | EN 196 | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | confirmation of water capillary absorption, 30min 28 days | Each lot | Karsten Tube | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | Confirmation of water retentively | Each lot | DIN 18555-7 | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | B) Application of paint | [8 empty] | Completed
|  | Confirmation of material with requires shad/RAL no. | Each lot | Client Reference | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
|  | Check for the surface cleaning from all masking tape, loos mortar, etc. | Each structure |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of marking for 1st coat, 2nd coat, & finish coat | Each structure | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for time between paint deferent coats | Each structure | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of final coat finishing and shad | Each structure | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for flaking /cracking /Sagging /Blistering | Each structure | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for stick for foreign matter | Each structure | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of physical and chemical properties | Each lot | Manufacturer Specification | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC | Completed
18 | Paver Block Laying | Required Safety norms coordinate to HSEM Process. |  |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for sand bed thickness |  | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for paver block laying pattern |  | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check for paver block top finished level |  | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of compressive strength | Each lot | IS 15658 | Site Lab | QA/QC Engr | QA/QC Engr | Review | Random | Test Report | Completed
|  | Confirmation of dimension | Each lot | IS 15658 | Site Lab | QA/QC Engr | QA/QC Engr | Review | Random | Test Report | Completed
|  | Confirmation of water observation | Each lot | IS 15658 | Site Lab | QA/QC Engr | QA/QC Engr | Review | Random | Test Report | Completed
19 | Water Proofing | Required Safety norms coordinate to HSEM Process. |  |  |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of material | Each lot | Client Reference | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC/Technical Data Sheet | Completed
|  | Confirmation of application method |  | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of surface preparation according to manufacturer specification |  | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Check weather all the opening/cutouts are sealed off as per requirement |  | Approved Drawing |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of completion of waterproofing with required coats/application of material up to required level/depth before expedite further activity |  | Manufacturer Technical Data Sheet |  | Site Engr | QC Engr | Witness | Random | Work Check List | Completed
|  | Confirmation of material physical and chemical properties | Each lot | Manufacturer Technical Data Sheet | Manufacturer | QA/QC Engr | QA/QC Engr | Review | Random | MTC/Technical Data Sheet | Completed