## 1
CHECKLIST FOR TRANSFORMER
Project
Report No. |  |  | Date of Inspection:
Ref.Drg.No.
S.No. | Description of Activity |  |  | YES | NO | Remarks
1 | Verify transformer make, kVA rating, vector group, and serial number against approved datasheet.
2 | Check transformer foundation, plinth level, vibration pads, and oil pit/soak pit construction as per standard.
3 | Confirm HT and LT bushing terminations are tightened, crimped, tagged, and shrouded properly.
4 | Ensure transformer neutral and body connected to two independent earth pits with correct conductor size.
5 | Verify transformer oil level, dielectric strength (BDV > 60 kV), and silica gel color (blue, not pink).
6 | Confirm radiator fins, cooling fans (ONAN/ONAF), and temperature gauges are installed and operational.
7 | Conduct insulation resistance (IR) test, turns ratio (TTR) test, and vector group test with recorded results.
Corrective Action Any :
Contractor |  |  | PMC
Name: |  |  | Name:
Date: |  |  | Date:
Approved
Not Approved
Approved With Comments