## 5
CHECKLIST FOR FINAL TESTING & COMMISSIONING
Project
Report No. |  |  | Date of Inspection:
Ref.Drg.No.
S.No. | Description of Activity |  |  | YES | NO | Remarks
1 | Hydrostatic test of hydrant and sprinkler piping witnessed and approved.
2 | Pump room testing: auto start of jockey pump at low pressure, main pump start at lower set, diesel pump auto start on power failure.
3 | Check pump shutoff head, rated duty point, and flow test with calibrated flow meter.
4 | Confirm fire water tank filling, overflow, drain, and level indicator functioning.
5 | Sprinkler discharge test conducted at remote end for spray pattern and coverage.
6 | Fire alarm cause-and-effect matrix tested: MCP, smoke detector, hooter, AHU shutdown, fire pump start.
7 | Verify monitoring signals integrated with Building Management System (BMS).
8 | Conduct full load trial of fire pump for 2 hours continuous run.
9 | Record all operating parameters (pressure, flow, voltage, current, alarms).
10 | Submit commissioning report, test certificates, and O&M manuals.
11 | Obtain consultant/fire authority approval and handover system to client.
Corrective Action Any :
Contractor |  |  | PMC
Name: |  |  | Name:
Date: |  |  | Date:
Approved
Not Approved
Approved With Comments